## Electrical BoQ
CSIR BIDF - Estimated Electrical Bill of Quantities |  |  |  | Project |  | CSIR BIDF
|  |  |  | Doc Nr |  | 21050-CSI-EC&I-RPT-002
Date | Done By: |  |  | Approved By |  | Details
17/09/2021 | K Freese |  |  | D Roode |  | Issued for Internal Review
G Stirling
BILL | DESCRIPTION | UNIT | QTY | RATE | AMOUNT (EXCL VAT) | AMOUNT (INCL VAT)
E1 | Distribution Board - (380V, 50Hz,1500A)
E1.1 | DB-01 | No. | 1
E.2 | LV Power Distribution Cable
E2.1 | EPCM Panel (DB-01) - 120mm2 4C SWA | m | 10
E2.2 | Parr Stirred Digester (19L) - 25mm2 3C SWA | m | 55
E2.3 | Low Consistency Refiner System - 25mm2 4C SWA | m | 18
E2.4 | Screen - 25mm2 3C SWA | m | 22
E2.5 | Bench-scale Biochar Unit - 25mm2 3C SWA | m | 30
E2.6 | Laboratory Woodchipper - 25mm2 3C SWA | m | 26
E2.7 | RDH Digester - 25mm2 4C SWA | m | 42
E2.8 | Flow-Through Digester - 25mm2 3C SWA | m | 63
E2.9 | Hemp Cleaner Digester - 25mm2 3C SWA | m | 18
E2.10 | Boiler - 25mm2 4C SWA | m | 63
E2.11 | Wastepaper Recycling Pilot - 25mm2 3C SWA | m | 5
E2.12 | Pilot-Scale Biochar Unit - 25mm2 4C SWA | m | 33
E2.13 | Valley Beater - 25mm2 3C SWA | m | 22
E2.14 | Compressor - 25mm2 4C SWA | m | 63
E2.15 | Oxidizer - 25mm2 4C SWA | m | 63
E2.16 | Lighting Circuitry - 4mm2 3C SWA | m | 800
E3 | Earthing Cable - ICW
E3.1 | 2000kVA, 5kV-480/277V Supply Cable - 70mm2 PVC | m | 130
E4 | LV Cable Terminations
E4.1 | EPCM Panel (DB-01) - 120mm2 4C SWA | No. | 2
E4.2 | Parr Stirred Digester (19L) - 25mm2 3C SWA | No. | 2
E4.3 | Low Consistency Refiner System - 25mm2 4C SWA | No. | 2
E4.4 | Screen - 25mm2 3C SWA | No. | 2
E4.5 | Bench-scale Biochar Unit - 25mm2 3C SWA | No. | 2
E4.6 | Laboratory Woodchipper - 25mm2 3C SWA | No. | 2
E4.7 | RDH Digester - 25mm2 4C SWA | No. | 2
E4.8 | Flow-Through Digester - 25mm2 3C SWA | No. | 2
E4.9 | Hemp Cleaner Digester - 25mm2 3C SWA | No. | 2
E4.10 | Boiler - 25mm2 4C SWA | No. | 2
E4.11 | Wastepaper Recycling Pilot - 25mm2 3C SWA | No. | 2
E4.12 | Pilot-Scale Biochar Unit - 25mm2 4C SWA | No. | 2
E4.13 | Valley Beater - 25mm2 3C SWA | No. | 2
E4.14 | Compressor - 25mm2 4C SWA | No. | 2
E4.15 | Oxidizer - 25mm2 4C SWA | No. | 2
E4.16 | Lighting Circuitry - 4mm2 3C SWA | No. | 48
E5 | Cable Trays and Racking
E5.1 | Cable Trays and Racking | m | 100
E5.2 | Cable Trays and Racking accessories | Lot | 1
E6 | Earthing and Lightning Protection
E6.1 | Earthing and Lightning Protection Material | Lot | 1
E6.2 | Earthing and Lightning Protection Testing and Reports | Lot | 1
E7 | Lighting and Small Power
E7.1 | Site Lighting (Suitable for use in Zone 2) | No. | 24
E8.1 | Installation & Commissioning (est)
TOTAL
Sub-Total
VAT 15%
TOTAL

## Instrumentation BoQ
CSIR BIDF - Estimated Instrumentation Bill of Quantities |  |  |  | Project |  | CSIR BIDF
|  |  |  | Doc Nr |  | 21050-CSI-EC&I-RPT-002
Date | Done By: |  |  | Approved By |  | Details
17/09/2021 | K Freese |  |  | D Roode |  | Issued for Internal Review
G Stirling
BILL | DESCRIPTION | UNIT | QTY | RATE | AMOUNT (EXCL VAT) | AMOUNT (INCL VAT)
Equipment Installation, Inspection and Calibration
I1 | Flow Meters
I1.1 | Volumetric Piston Rotary Water Meters | Lot | 1
I2 | Temperature Instrumentation
I2.1 | Temperature Gauges | Lot | 1
I3 | Pressure Instrumentation
I3.1 | Pressure Gauges | Lot | 1
I4.1 | Installation & Commissioning (est)
New Equipment
I5 | Flow Meters
I5.1 | Volumetric Piston Rotary Water Meters | No | 2
I6 | Temperature Instrumentation
I6.1 | Temperature Gauges | No | 2
I7 | Pressure Instrumentation
I7.1 | Pressure Gauges | No | 11
Sub-Total
VAT 15%
TOTAL

## Mechanical & Piping BOQ
CSIR BIDF - Estimated Mechanical & Piping Bill of Quantities |  |  |  | Project |  | CSIR BIDF
|  |  |  | Doc Nr |  | 21050-CSI-EC&I-RPT-002
Date | Done By: |  |  | Approved By |  | Details
17/09/2021 | M Joubert |  |  | D Roode |  | Issued for tender purposes
G Stirling
BILL | DESCRIPTION | UNIT | QTY | RATE | AMOUNT (EXCL VAT) | AMOUNT (INCL VAT)
Mechanical Equipment
M1 | Electric Steam Boiler (KSM Boiler and Plant Solutions)
M1.1 | 300kg/h Marshal Fowler ES 20 Steam Generator | No. | 1
Piping, Valves and Connections
M2 | Valves
M2.1 | Steam Line 1/2" Socket Weld Stop Valves (ASME B16.34 / API 608 or similar) | qty | 8
M2.2 | Steam Line 1 1/2" Socket Weld Stop Valves (ASME B16.34 / API 608 or similar) | qty | 1
M2.3 | Nitrogen Line 3/8" BSP Ball Valves (EN 331) | qty | 3
M2.4 | Compressed Air Line 1/2" BSP Ball Valves (EN 331) | qty | 5
M2.5 | Municipal Water Line 15mm BSP Ball Valves (EN 331) | qty | 12
M2.6 | Hot Geyser water Line 15mm BSP Ball Valves (EN 331) | qty | 4
M2.7 | Hot Geyser water Line 22mm BSP Ball Valves (EN 331) | qty | 1
M2.8 | Steam Line 1 1/2" Socket Weld Plug Valves (ASME B16.34 / API 6D) | qty | 1
M2.9 | Steam Line 3/8" Socket Weld Needle Valve (ASME 16.34 / API 594) | qty | 1
M3 | Piping and Connections
Steam lines
M3.1 | ASME 31.3 CS A106 Gr B SCH 40 1 1/2" | m | 36
M3.2 | ASME 31.3 CS A106 Gr B SCH 40 1/2" | m | 12
M3.3 | ASME 31.3 CS A106 Gr B SCH 40 3/8" | m | 12
M4 | Steam Fittings
M4.1 | EN1092 PN25 RF Blind Flange (#5) IMPERIAL 2" RF BLIND FLANGE 2" | qty | 1
M4.2 | End Caps A106 Gr B CS SCH40 Pipe Connection SW 1 1/2" | qty | 4
M4.3 | End Caps A106 Gr B CS SCH40 Pipe Connection SW 3/8" | qty | 1
M4.4 | Reducing Tee-Piece A106 Gr B CS SCH40 SW x A106 Gr B CS SCH40 SW 2x1.5" Pipe by 1x3/8" Pipe | qty | 1
M4.5 | Reducing Tee-Piece A106 Gr B CS SCH40 SWx A106 Gr B CS SCH40 SW 2x1.5" Pipe by 1x1/2" Pipe | qty | 2
M4.6 | 90 degree Angles A106 Gr B CS SCH40 SW x A106 Gr B CS SCH40 SW 1.5" Pipe x 1.5" Pipe | qty | 4
M4.7 | 90 degree Angles A106 Gr B CS SCH40 SW x A106 Gr B CS SCH40 SW 0.5" Pipe x 0.5" Pipe | qty | 12
M4.8 | EN1092 PN25 RF Slip On Flange (#1) IMPERIAL 1.5" RF SLIP ON FLANGE 1.5" | qty | 2
M4.9 | EN1092 NP25 RF Blind Flange (#5) IMPERIAL 1.5" RF BLIND FLANGE 1.5" | qty | 2
M4.10 | Tee-Piece A106 Gr B CS SCH40 SWx A106 Gr B CS SCH40 SW 1.5" | qty | 5
M4.11 | Tee-Piece A106 Gr B CS SCH40 SWx A106 Gr B CS SCH40 SW 0.5" | qty | 6
M4.12 | EN1092 PN40 RF Slip On Flange (#1) METRIC DN20 RF Slip on Flange DN20 | qty | 1
M5 | Hot Water Lines
M5.1 | SANS 460/2 22mm Copper Tubing | m | 5.5
M5.2 | SANS 460/2 15mm Copper tubing | m | 55
M6 | Hot Water Fittings
M6.1 | End Caps Cu Tube Connection 15mm | qty | 2
M6.2 | End Caps Cu Tube Connection 22mm | qty | 2
M6.3 | Reducing Straight Coupler 2 x Cu Tube Connection 15mm x 22mm | qty | 3
M6.4 | Tee Piece 3 x Cu Tube Connection 22mm | qty | 1
M6.5 | Elbow 2 x Cu Tube Connection 22mm | qty | 5
M6.6 | Elbow 2 x Cu Tube Connection 15mm | qty | 10
M6.7 | Male Connector Cu Threaded End x Cu Tube Connection 3/4" BSPP x 22mm Tube | qty | 2
M6.8 | Male Connector Cu Threaded End x Cu Tube Connection 3/4" BSPP x 15mm Tube | qty | 8
M6.9 | Female Connector Cu Tube Connection x Cu Threaded End 15mm Tube x 3/4" BSP Thread | qty | 2
M6.10 | Male Connector Cu Threaded End x Cu Tube Connection 3/4" BSPP x 15mm Tube | qty | 2
M6.11 | Female Connector Cu Tube Connection x Cu Threaded End 15mm Tube x 3/4"BSP Thread | qty | 2
M7 | Municipal Water Lines
M7.1 | SANS 460/2 15mm | m | 66
M7.2 | ASME 36.19 SS304 SCH 40 1/2" | m | 5.5m
M7.3 | ASME 36.19 SS316 SCH 40 1" | m | 5.5m
M7.4 | ASME 36.19 SS316 SCH 40 20mm | m | 5.5m
M8 | Municipal Water Fittings
M8.1 | End Caps Cu Tube Connection 15mm | qty | 5
M8.2 | Tee Piece 3 x Cu Tube Connection 15mm | qty | 10
M8.3 | Elbow 2 x Cu Tube Connection 15mm | qty | 15
M8.4 | Male Connector Cu Threaded End x Cu Tube Connection 3/4 BSPP male x 15mm Tube | qty | 26
M8.5 | Female Connector Cu Tube Connection x Cu Threaded End 15mm Tube x 1/2" BSPF Thread | qty | 1
M8.6 | Male connector 6mm x 1/2" BSP Male Pushin Fittings 6mm x 1/2" BSP Male Pushin Fittings | qty | 1
M8.7 | Female Connector Cu Tube Connection x Cu Threaded End 15mm Tube x 1/2" BSPF Thread | qty | 1
M8.8 | Male connector 6mm x 1/2" BSP Male Pushin Fittings 6mm x 1/2" BSP Male Pushin Fittings | qty | 1
M8.9 | Male Connector Cu Tube Connection x Cu Threaded End 15mm Tube x 25mm BSP Thread | qty | 1
M8.10 | EN1092 SS PN40 Blind (#05) Flange DN25 SS316L Flange DN25 | qty | 1
M8.11 | Male Connector 15MM x 3/4 Male connector To Connect for female threaded flange | qty | 1
M8.12 | EN1092 SS PN40 Weldneck (#11) Flange DN25 (1inch) SS 316L Flange DN25 | qty | 1
M8.13 | Male Connector SS 316L Pipe x SS 316L Threaded End 1" SS Tube x 1" NPT Thread | qty | 1
M8.14 | Male Connector Cu Tube Connection x Cu Threaded End 15mm Tube x 15mm BSP Thread | qty | 1
M8.15 | EN1092 SS PN25 Blind (#05) Flange (IMPERIAL) 1" SS304 Flange 1/2" | qty | 1
M8.16 | EN1092 SS PN25 Weldneck (#11) Flange IMPERIAL 1" SS304 Flange 1/2" | qty | 1
M8.17 | Female Connector SS306 SCH40 Pipe Connection x Threaded End 1/2" Pipe Connection x 1/2" BSP Thread | qty | 1
M8.18 | Tee Piece SS316L Pipe connection x SS316L Pipe connection 20mm SS Pipe x 20mm SS Pipe | qty | 1
M8.19 | Elbow SS316L Pipe connection x SS316L Pipe connection 20mm SS Pipe x 20mm SS Pipe | qty | 6
M8.20 | Male Connector Cu Tube Connection x Cu Threaded End 15mm Tube x 20mm BSP Thread | qty | 1
M8.21 | EN1092 SS PN40 Blind (#05) Flange METRIC DN20 SS316L Flange DN20 | qty | 1
M8.22 | EN1092 SS PN40 Weldneck (#11) Flange METRIC DN20 SS 316L Flange DN20 | qty | 3
M8.23 | Reducing Female Coupler Brass Threaded End x Cu Tube Connection 3/4" BSP Thread x 15mm Cu Tube | qty | 1
M9 | Compressed Air Lines
M9.1 | Medical Cu Tube 1/2" Medical Grade Copper Tubing 1/2" | m | 38.5
M9.2
M9.3 | Compressed Air Fittings
M9.4 | Male Connector 12/" tube x 1/2" NPT 1/2" | qty | 2
M9.5 | Plug 1/2" NPT Plug 1/2" | qty | 2
M9.6 | Tee Piece 3 x Cu Tube Connection 1/2" | qty | 7
M9.7 | Elbow 2 x Cu Tube Connection 1/2" | qty | 10
M9.8 | Male Connector Cu Threaded End x Cu Tube Connection 1/2" NPT x 1/2" Tube | qty | 10
M9.9 | Female Connector Cu Threaded End x Cu Tube Connection 3/8" NPT x 1/2" Tube | qty | 2
M9.10 | Reducing Union Threaded End x Flex Hose Nipple 1/2" Tube x 3/8" Tube | qty | 2
M9.11 | Female Connector Cu Threaded End x Cu Tube Connection 1/4" NPT x 1/2" Tube | qty | 1
M9.12 | Male Quickfit Nipple Threaded End x Flex Hose Nipple 1/2" Tube x 3/8" Tube | qty | 1
M9.13 | Straight Coupler Medical copper Tube x SS316 Tube 1/2" Tube x 3/8" Tube | qty | 1
M9.14 | Male Connector SS Threaded End x SS316 Tube 3/8" BSPP x 3/8" Tube | qty | 1
M10 | Nitrogen Lines
M10.1 | Medical Cu Tube 3/8" | m | 30.48
M11 | Nitrogen Fittings
M11.1 | Male connector 3/8" tube X 1/2" npt male 3/8" | qty | 2
M11.2 | Male Plug 1/2" 1/2" | qty | 2
M11.3 | Tee Piece 3 x Cu Tube Connection 3/8" | qty | 7
M11.4 | Elbow 2 x Cu Tube Connection 3/8" | qty | 6
M11.5 | Male Connector Cu Threaded End x Cu Tube Connection 1/2" NPT x 3/8" Tube | qty | 6
M11.6 | Female Connector Threaded End x Cu Tube Connection 1/4" NPT x 3/8" Tube | qty | 1
M11.7 | Straight Coupler Medical copper Tube x SS316 Tube 3/8" Tube x 3/8" Tube | qty | 1
M11.8 | Male Connector SS Threaded End x SS316 Tube 3/8" BSPP x 3/8" Tube | qty | 1
Strainers
M12.1 | Spirax Sarco Y-Tipe Strainer (0.5" Socket Weld Ends - ASME SCH 40 Pipe) | qty | 2
Steam Line Air Vent
M12.1 | Thermostatic Air Vent (1.5" Socket Weld Ends - ASME SCH 40 Pipe) | qty | 1
Thermodynamic Steam Trap
M14.1 | Thermodynamic Steam Trap (0.5" Socket Weld Ends - ASME SCH 40 Pipe) | qty | 2
Sub-Total
VAT 15%
TOTAL

## Civil & Structural BoQ
CSIR CANOPY - Preliminary Bill of Quanities |  |  |  | Project |  | CSIR CANOPY
Doc Nr
Date: 2021/10/19 | Done By: |  |  | Approved By |  | Details
| R. van Aswegen |  |  |  |  | Issued for Internal Review
| G Stirling |  |  | D. Roode |  | issued for Client Review
BILL | DESCRIPTION | UNIT | QTY | RATE | AMOUNT (EXCL VAT) | AMOUNT (INCL VAT)
SECTION NO. 1
BILL NO. 1
ALTERATIONS and DEMOLITIONS
PREAMBLES
For Preambles see "Model Preambles For Trades"
SUPPLEMENTARY PREAMBLES
View site
Before submitting his tender the tenderer shall visit the site and satisfy himself as to the nature and extent of the work to be done and the value of the materials salvageable from the alterations. No claim for any variations of the contract sum in respect of the nature and extent of the work or of inferior or damaged materials will be entertained.
Explosives
No explosives whatsoever may be used for alteration purposes unless otherwise stated
General
The contractor shall carry out the whole of the works with as little mess and noise as possible and with a minimum of disturbance to tenants in the building and to adjoining premises and their tenants. He shall provide proper protection and provide, erect and remove whendirected, any temporary tarpaulins that may be necessary during the progress of the works, all to the satisfaction of the principle agent. Doors, fanlights, windows, fittings, frames, linings, etc which are to remain the property of the employer shall be carefully taken out, temporarily stored, transported over a distance approximately 5km to store and handed over to employer. Doors, fanlights, windows, fittings, frames, linings, etc which are to be re-used shall be thoroughly overhauled before re-fixing including taking off, easing and re-hanging, cramping up, re-wedging as required and making good cramps, dowels, etc, and oiling, adjusting and repairing ironmongery as necessary, replacing any glass damaged in removal or subsequently and stopping up all nail and screw holes with tinted plastic wood to match timber, unless otherwise described. Re-painting or re-varnishing is given separately. Prices for taking out of doors, windows, etc shall include for removal of all beads, architraves, ironmongery, etc. Prices for taking out and removing doors and frames shall include for removing door stops, cabin hooks, etc. With regards to building up openings in existing walls, cement screeds and pavings, granolithic, tops of walls, etc, shall be levelled and prepared for raising of brickwork. Making good of finishes shall include making good of the brick and concrete surfaces onto which the new finishes are applied, where necessary. Thecontractor will be required to take all dimensions affecting the existing buildings on site and he will be held solely responsible for the accuracy of all such dimensions where used in the manufacture of new items (doors, windows, fittings, etc).
ROOF SLAB
ALTERATIONS and DEMOLITIONS
REMOVAL OF EXISTING WORK
Taking down and removing roofs, floors, panelling, ceilings, partitions, etc
C1.1 | Existing waterproofing | m2 | 338.6748
C1.2 | Removal of existing screed 100mm to 50mm (75mm average thickness) | m2 | 338.6748
| DEMOLITIONS AND ALTERATIONS |  |  |  |  | 0
SECTION NO. 1
BILL NO. 2
ROOF COVERINGS ETC
PREAMBLES
For Preambles see "Model Preambles For Trades"
SUPPLEMENTARY PREAMBLES
Guarantee
The contractor is to state the period and level of guarantee of workmanship and materials for this project in his tender.
Availability of materials
The contractor is to ascertain what materials and quantities are available for this project and state this in his tender
Manpower
The contractors is to state availability of his own resources for this project in his tender
Straight cutting
Descriptions of all roof coverings are deemed to include for all straight cutting
C2 | PROFILED METAL SHEETING
IBR Roof Sheeting as per engineer specification
C2.1 | 0.8mm IBR Roof Sheeting | m2 | 320.9728
Extra over Roof sheeting for
C2.2 | Clear roof sheeting as per engineers specification | m2 | 44
IBR Side cladding as per engineer specification
C2.3 | 0.8mm IBR Side Cladding | m2 | 410
METAL SHEET ACCESSORIES
IBR Roof Sheeting as per engineer specification
C2.4 | Ridge cap flashing 620mmg | m | 30
C2.5 | Drip Flashing | m | 82
C2.6 | Whirley Birds | No | 6
| ROOF COVERINGS |  |  |  |  | 0
SECTION NO. 1
BILL NO. 3
STRUCTURAL STEELWORK
SUPPLEMENTARY PREAMBLES
Descriptions Descriptions of bolts shall be deemed to include nuts and washers Descriptions of expansion anchors and bolts and chemical anchors and bolts shall be deemed to include nuts, washers and mortices in brickwork or concrete
Descriptions of L-shaped and U-shaped anchor bolts shall be deemed to include bending, threading, nuts and washers and embedding in concrete. Where anchor bolts are described as embedded in sides or soffits of concrete it shall be deemed to include holes through formwork.
C3 | STEEL ROOF CONSTRUCTION (PROVISIONAL)
C3.1 | Steel Canopy Structure | t | 14.97
C3.2 | Bolts & Plates | t | 1.497
Chemical anchors
C3.3 | Hilti HIT-RE 500 met HIT-V rod (16 mm) | No | 96
| STRUCTURAL STEELWORK |  |  |  |  | 0
SECTION NO. 1
BILL NO. 4
METALWORK
PREAMBLES
For preambles see "Model Preambles for Trades"
C4 | MILD STEEL BALUSTRADES, HANDRAILS ETC
Painted mild steel collapsable balustrade (Colour TBC) including 42mm diameter mild steel top handrail and 4mm steel cables complete as per Architect specification
C4.1 | 1000mm high Straight Collapsable Handrails | m | 6
STEEL SLIDING DOORS
Double sliding doors with glossy non-drip enamel finish. Colour: Charcoal including ironmongery
C4.2 | S1 - Double steel sliding door including top and bottom track | No | 1
MILD STEEL DOORS
Double door with glossy non-drip enamel finish. Colour: Charcoal including ironmongery
C4.3 | D1 - 1640 x 2083mm high overall including frame fixed to structural steel | No | 1
| METALWORK |  |  |  |  | 0
SECTION NO. 1
BILL NO. 5
CEILINGS, PARTITIONS AND ACCESS FLOORING
PREAMBLES
For Preambles see "Model Preambles For Trades"
INSULATION
C5 | Insulation to roofs
C5.1 | Sisalation Roof insulation | m2 | 330
PARTITIONS, ETC
Solid drywall or similar approved partition systems
107 - PARTITIONS
Gyproc Saint-Gobain Rhinoboard Firestop drywall partitioning shall comprise steel studding formed of 2 x 102 x 35mm Donn UltraSteel drywall top and bottom tracks with vertical studs at maximum 600mm centres, friction fitted or pop-riveted to the top and bottom tracks with similar additional vertical studs as necessary at abutments, ends, etc.with 102mm "Isover cavitylite" insulation inserted into cavity of partition and covered on both sides with 2 layers 15mm "Rhinoboard Firestop" per manufacturer, all screwed to studding with "Drywall" screws at maximum 220mm centres. Boards are to be butt jointed and finished with "Rhino" tape and "Readymix D" jointing compound. The panels are to be completely skim coated on both sides (paint to both sides elsewhere measured), all according to manufacturer's specifications. Intersections and abutments are measured separately and descriptions shall be deemed to include any additional studs, corner beads, jointing compound, tape, etc.
C5.2 | Drywall partition 4,95m high with bottom track plugged and top track fixed to roof sheeting tees | m | 29.155
C5.3 | Extra over for standard size partition door | No | 2
| CEILINGS, PARTITIONS AND ACCESS FLOORING |  |  |  |  | 0
SECTION NO. 1
BILL NO. 6
FLOOR COVERINGS, WALL LININGS, ETC
PREAMBLES
For Preambles see "Model Preambles For Trades"
Notes to Tenderers
Moisture test must be done before any preparations starts (THIS MUST BE DONE TIMEOUSLY IN ORDER TO AVOID TIME LOSS OR ADDITIONAL COST)
Full project pack to be issued to Client on completion with all guarantees and maintenance manuals (Supplied by Manufacturer and Supplier).
POLISH, SEALERS, ETC
Sweep, clean with detergent complying with SABS 825, rinse and apply three coats of water emulsion polish complying with SABS 1042, including buffing after application of each coat of polish
C6.1 | On exposed slab where screed was removed | m2 | 338.6748
FLOOR COVERINGS
6mm Polyurethane floor screed
C6.2 | On floors | m2 | 338.6748
C6.3 | 10mm joints | m | 96
| FLOOR COVERINGS, WALL LININGS, ETC |  |  |  |  | 0
SECTION NO. 1
BILL NO. 7
PLUMBING AND DRAINAGE
PREAMBLES
For Preambles see "Model Preambles For Trades"
SUPPLEMENTARY PREAMBLES
uPVC pipes and fittings
Sewer and drainage pipes and fittings shall be jointed and sealed with butyl rubber rings
Soil, waste, vent pipes and fittings shall be solvent weld jointed
uPVC pressure pipes and fittings
Pipes for water supply shall be of the class stated
Pipes of 40mm diameter and smaller shall be plain ended with solvent welded uPVC loose sockets and fittings
Pipes of 50mm diameter and greater shall have sockets and spigots with push in type integral rubber ring joints. Bends shall be uPVC and all other fittings shall be cast iron, all with similar push-in type joints
Copper pipes
Pipes shall be hard drawn and half-hard pipes of the class stated. Class 0 (thin walled hard drawn) pipes shall not be bent. Class 1 (thin walled half-hard), class 2 (half-hard) and class 3 (heavy walled half-hard) pipes shall only be bent with benders with inner and outer formers. Capillary solder fittings shall comply with ISO 2016. Only compression fittings shall be used in walls or in ground
Fixing of pipes
Unless specifically otherwise stated, descriptions of pipes shall be deemed to include fixing to walls etc, casting in, building in or suspending not exceeding 1m below suspension level
Reducing fittings
Where fittings have reducing ends or branches they are described as "reducing". In the case of pipes with diameters not exceeding 60mm only the largest end or branch size is given. Should the contractor wish to use other fittings and bushes or reducers he may do so on the understanding that no claim in this regard will be entertained. In the case of pipes with diameters exceeding 60mm all sizes are given and no claim for extra bushes, reducers, etc will be entertained
In the case of pipes with diameters exceeding 60mm all sizes are given and no claim for extra bushes, reducers, etc will be entertained
Excavations
No claim for rock excavation will be entertained unless the contractor has timorously notified the Principal Agent thereof prior to backfilling
Soft rock and "hard rock" shall be as defined in "Earthworks"
Laying, backfilling, bedding, etc of pipes
Pipes shall be laid and bedded and trenches shall be carefully backfilled in accordance with manufacturers' instructions
Where no manufactures' instructions exist pipes shall be laid in accordance with clause 5.1 and 5.2 of each of the following: SABS 1200 L : Medium-pressure pipelines LD : Sewers LE : Stormwater drainage
Pipe trenches etc shall be backfilled in accordance with clause 3.1 to 3.4.1, 5.1 to 5.3 and 7 of SABS 1200 LB : Bedding (Pipes).
Unless otherwise described bedding of rigid pipes shall be class B bedding
Flush pans
Flush pans shall have straight or side outlets and "P" or "S" traps as necessary
Stainless steelbasins, sinks, wash troughs, urinals, etc.
Units shall have standard aprons on all exposed edges and tiling keys against walls where applicable
Waste unions
Descriptions of waste unions shall be deemed to include rubber or vulcanite plugs and chains fixed to fittings
RAINWATER DISPOSAL
C7 | Seamless epoxy coated aluminium gutters and rainwater downpipes fixed to GMS rafter and face of inner wall and supported on steel roof structure to fall
C7.1 | 200 x 150mm Gutter | m | 60
C7.2 | 100 x 3mm RWDP | m | 30
C7.3 | Extra over for bends | No | 12
C7.4 | Extra over for shoe | No | 6
SANITARY FITTINGS
Sanitary fittings
Comprises fittings and units complete with, service pipes, stop cocks and traps and those combined with cupboards or worktops excluding taps and mixers.
C7.5 | Double Bowl sink | No | 1
Sanitary fittings sundries
Comprises soap dishes, toilet paper holders, mirrors, towel rails, medicine cabinets, etc.
C7.6 | Soap dish | No | 1
SANITARY PLUMBING
Sanitary plumbing
Comprises anti-siphonage, waste, soil and vent stacks, paint on pipes, a proportion of holes and cutting to tiling, etc.
C7.7 | Sanitary plumbing | No | 1
Cold water supplies
Comprises all cold water services including paint on pipes, a proportion of holes and cutting to tiling, wheel valves, etc.
C7.8 | Cold water supplies | No | 1
Hot water supplies
Comprises piping, lagging, paint on pipes, a proportion of holes and cutting to tiling, wheel valves, etc.
C7.9 | Hot water supplies | No | 1
ELECTRIC WATER HEATERS
Manufactured by "Kwikot"
C7.10 | 100 Litre roof mounted solar water heater | No | 1
FIRE APPLIANCES, ETC
C7.11 | 4.5kg Dry chemical powder fire extinguisher including backing board | No | 4
Fire hose reel including all necessary pipework, fittings, bends, tees, reducers and sundries complete in accordance with SANS standards
C7.12 | Fire hose reel with 30m rubber hose, chromium plated stopcock, shut-off nozzle, wall bracket, nipples, flanges, etc to fix to water supply pipe. Complete. | No | 2
uPVC Class 16 pipes
C7.13 | 50mm Fire water supply pipes laid in earth or in earth filling under surface beds, including excavations not exceeding 1m deep | m | 30
Extra over uPVC Class 16 pipes for compression fittings
C7.14 | 50mm Bend | No | 6
TESTING
C7.15 | Testing water supply system to fire appliances | Item | 1
| PLUMBING AND DRAINAGE |  |  |  |  | 0
SECTION NO. 1
BILL NO. 8
PAINTWORK
PREAMBLES
For Preambles see "Model Preambles For Trades"
PAINTWORK, ETC TO NEW WORK ON
PLASTER BOARD SURFACES
One coat alkali resistant plaster primer and two coats "Dulux Trade" PVA acrylic emulsion paint on
C8.1 | Drywall | m2 | 288.6345
| PAINTWORK |  |  |  |  | 0
Sub-Total
VAT 15%
| TOTAL |  |  |  |  | 0