## Boiler Data
Project |  | Building and Management Services for Modification of Pilot Plant |  |  |  |  | Page 1 of 5
Document No. |  | 21050-CSI-ME-DAS-003
Location |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Boiler
Revision Status
Rev No. |  | Date | Prepared By | Revised Sheet | Revision | Approvals
[6 empty] | Checked By | Approved By
A |  | 2021-09-01 | M.J | All | Issued for Internal Review
NOTES
1 | VTC - Vendor to Confirm
1 | Description |  |  | Electric Steam Boiler
2 | Reference P&ID |  |  | 21050-CSI-PR-PID-012 -REV O.pdf
3 | Country of Origin |  |  | South Africa
4 | Quantity: |  |  | 1
5 | Service: |  |  | Minimum 300kg/hr Steam Production to BIDF Laboratory
6 | Fuel: |  |  | Electric
8 | Pressure: |  | min: | 0 |  |  |  | kPa
|  |  | Operating | 1200 |  |  |  | kPa
|  |  | max: | 1700 |  |  |  | kPa
|  |  | design: | VTC |  |  |  | kPa
9 | Temperature: |  | min: | 0 |  |  |  | oC
|  |  | max: | 200 |  |  |  | oC
|  |  | design (min/max): | 0/211 |  |  |  | oC
10 | Feed Rate: |  | min: | 100 |  |  |  | kg/hr
|  |  | max: | 300 |  |  |  | kg/hr
|  |  | design: | VTC |  |  |  | kPa
11 | Max Time to Steam Production:
12 | Supply voltage:
13 | Power Usage for Steam Production |  |  | 1 |  |  |  | kW/kg
15 | Feed Water Tank Included |  | Y/N | Y
14 | Max Allowable Outer Dimensions: (INCLUDES ALL BOILER TANKS and Maintenance Space required.) |  | Length: | 1510 |  |  |  | mm
|  |  | Width: | 1210 |  |  |  | mm
|  |  | Height: | 4400 |  |  |  | mm
15 | Weight |  |  | 1100 |  |  |  | kg
16 Boiler Element Protection | Design Code: |  |  | EN 1293-2002
17 | Code of Manufacture:
18 | Safety Design Code:
22 | Material: |  | Vessel: |  |  | Class/Sch
Instrument Tubing
Piping
| Mounting: |  | Skid or Ground | VTC
24 | Lifting Lugs:
25 | Cradles/Leg supports: |  |  | Leg supports required (S-355 JR)
27 | Pressure Gauge |  |  | Pressure Gauges required?
27 | Safety Valve: |  |  | 1" BSP SCRD Safety Valve
28 | Bckup Safety: |  | Y/N | VTC
General Requirements
30 | 1 - Weld Quality Requirements in accordance with ISO 3834
31
32

## Additional Components
Project |  | Building and Management Services for Modification of Pilot Plant |  |  |  |  | Page 2 of 5
Document No. |  | 21050-CSI-ME-DAS-003
Location |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Boiler
Revision Status
Rev No. |  | Date | Prepared By | Revised Sheet | Revision | Approvals
[6 empty] | Checked By | Approved By
A |  | 2021-09-01 | M.J | All | Issued for Internal Review
NOTES
1 | VTC - Vendor to Confirm
1 | Water Softner: |  | Make
Model
Automatic/ Manual

## Connections
Project |  | Building and Management Services for Modification of Pilot Plant | [5 empty] | Page 3 of 5
Document No. |  | 21050-CSI-ME-DAS-003
Location |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Steam Boiler
Revision Status
Rev No. |  | Date | Prepared By | Revised Sheet | Revision |  | Approvals
[7 empty] | Checked By | Approved By
A |  | 2021-09-03 | M.J | All | Issued for Internal Review
1
2 |  | SKETCH AND/OR ADDITIONAL INFORMATON FROM PAGE 1
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
40 | Connection | Size | Type | Material | Thread | Class/Sch | Notes
41 | Main Water Inlet | 3/4" | Male Scrd Ball Valve | Brass | BSP | Class2 | Inlet at Ball Valve - Main Boiler Inlet
| Main Steam Outet | 2" | EN 1092 Flange 2500/3 | 430A Boiler Plate |  | Sch 160
43 | Safety Valve Outlet | 1" | Male Scrd Safety Valve | Bronze Safety Valve | BSP | Sch 40
| Blow Down Tank Drain | 1 1/2" | Scrd | Mild Steel | BSP | Sch 40
44 | Vent on Feed Tank | 2" | Scrd | Mild Steel | BSP | Sch 40
45 | Vent on Blowdown Tank | 2" | Scrd | Mild Steel | BSP | Sch 40
48 | General Requirements
49 | For Maintenance, the boiler requires a SWL 1.5 Tonne Crawl @ 2.7m above the boiler.
50 | Electricity Input (Plug?)
51 | Boiler House - VTC

## QA Inspection
Project |  | Building and Management Services for Modification of Pilot Plant |  |  |  | Page 4 of 5
Document No. |  | 21050-CSI-ME-DAS-003
Location |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
QA INSPECTION & TESTING
1 | QA TESTING & INSPECTION
2 |  |  | By Vendor | On Site | Witnessed | Comment
3 | Shop Inspection |  | X
5 | Hydraulic Test |  | X
6 | Calibration Test |  |  | X
7 | Performance test |  | X
8 | Retest on Seal leakage |  |  | X
9 | Test data approval |  | X
10 | Complete Unit Test |  | X
11 | Vibration Test |  | X
12 | Compliance with inspectors check list |  | X | X
13 | DRAWINGS and DOCUMENTS REQUIRED
14 | 1. GENERAL DOCUMENTS REQUIRED
15 | 1.1 The test data and performance for all above mentioned tests
16 | 1.2 Vendor to include mechanical seal drawings
17 | 1.3 Vendor to include general arrangement drawings.
18 | 1.4 Vendor to include list of start up and 2 year spares equirements?
19 | 2. DOCUMENTS REQUIRED
20 | Two copies of each of the following shall be submitted
21 | 2.1 All documents required by Procurement.
22 | 2.2 Completed technical specification (i.e. data sheets marked up where vendor information is required).
23 | 2.3 Overall time schedule - Procurement, Manufacture, Testing and Delivery.
24 | 3. DOCUMENTS REQUIRED AFTER ORDER PLACEMENT SHALL BE AS DESCRIBED ON PAGE 4 OF 5
27 | 3.1 All drawings shall have the title block unique for this project included on the drawing, located at the lower right hand side of the drawing.
28 | 3.2 For documents of A4 and A3 size, the title block shall be generally measuring 180 wide x 120 high.
29 | Standard title blocks to be incorporated into the general arrangement drawing will be given after order placement.
30 | 3.3 Drawings shall be either A3 or A4 sizes. No larger or smaller size drawings will be acceptable.
31 | A4 size paper will generally be used for parts lists.
32 | 3.4 Every drawing must carry the Project document number allocated to it.
33 | Document numbers shall be obtained by the vendor from Document Control Department.

## Eng Docs
Project: |  | CPMZ Pump Station Project |  |  |  | Page 5 of 5
Document No. |  | 19088-PS1-ME-DS-007
Location |  | Mozambique
ENGINEERING DOCS.
| ENGINEERING DOCUMENTS |  | DOCUMENTS APPLICABLE (Y/N) | DUE DATE (WEEKS AFTER ORDER) | COPIES REQUIRED WITH QUOTE (Y/N) | PAPER COPIES | ELECTRONIC COPIES
1 | A - DESIGN DOCUMENTS
2 | Catalogue / Manual |  | Y |  | N
3 | Materials List |  | Y |  | N
4 | Connection / Sectional Diagrams (incl. Auxillary Equipment and Seals) |  | Y |  | N
5 | Data Sheets |  | Y |  | N
6 | General Arrangement Drawings |  | Y |  | Y
7
8 | B - QUALITY ASSURANCE DOCUMENTS
9 | Quality Control Plans |  | Y |  | N
10 | Final Inspection Procedure |  | Y |  | N
11 | Packaging and Transport Procedure |  | Y |  | N
12
13 | C - FINAL DOCUMENTATION
14 | Code Data Books containing Documents as per Approved Index |  | Y |  | N
15 | Installation, Operating and Maintenance Manuals |  | Y |  | N
16
17 | D - INSTRUCTIONS AND NOTES TO SUPPLIER - ENGINEERING DOCUMENTS
18 | The Engineering and Final Documents listed above shall be furnished by the Manufacturer.
19 | Version and Delivery date shall be as specified.
20 | Wording shall be in the English language.
21 | All packages shall be complete. Packages lacking in detail will be returned without review to the Manufacturer.
22 | Column 1 is a list of possible documents required.
23 | Column 2 indicates the specific information required by CPMZ.
24 | Column 3 indicates the required document submission date after order award or release for delivery as applicable.
25 | Column 4 indicates if copies are required to be submitted with the Supplier’s quotation.
26 | Column 5 & 6 indicates the number of copies/prints of a document required.
27 | The base date for submittal of all documents is the effective date of the Purchase Order.
28 | All documentation must be submitted on white paper sheets with black script / details.
29 | All drawings/data submitted must be identified by marking with the Purchaser’s order number and equipment tag/item number(s).
30 | All A4 size documents must have a cover sheet containing the relevant contract data, document numbers as well as equipment tag numbers.
31 | Acceptable drawing sizes are A3 for sectional diagrams and A4 for unit and component technical drawings.
32 | Native versions of drawings to be submitted in AutoCAD format.
33 | Code Data Books and Manuals shall include Minute of Meetings, Test and Maintenance Acitivities as applicable.