## Sheet1
Project: |  | 21050 | [7 empty] | Revision Status | [11 empty] | Page 1 of 1
[10 empty] | Rev No. | Date |  | Prepared By | Revised Sheet | Comments |  |  | Approvals
Document No.: |  | 21050-CSI-PR-LST-001 | [15 empty] | Checked By |  | Approved By
[10 empty] | A | 11/08/2021 |  | YW | ALL | Issued for Internal Review |  |  | JB |  | JB
Location: |  | Glenwood, Durban | [7 empty] | B | 11/08/2021 |  | YW | ALL | Issued for Client Review |  |  | JB |  | JB
[10 empty] | 0 | 16/08/2021 |  | YW | ALL | Issued for Information |  |  | JB |  | JB
Battery Limit Schedule | [9 empty] | 1 | 02/09/2021 |  | JB | ALL | Issued for Information |  |  | YW |  | YW
No | Battery limit description |  | Drawing No | Fluid State | Connection Type | Pipe Material | Nominal Size | Wall Thickness/ Schedule | Design condition |  |  | Operating Condition | [8 empty] | Tie-In No | Remarks
[9 empty] | Line class | Temperature (℃) | Pressure (kPa(g)) | Flow |  |  | Design Temperature (℃) |  |  | Pressure (kPa(g))
[10 empty] | Min/Max | Min/Max | Min | Normal | Max | Min | Normal | Max | Min | Normal | Max
Parr Stirred Digestor
1 | Main Water Supply |  | 21050-CSI-PR-PID-002 | Liquid | Quick Fit | Poly urethane | 6X4 mm | 2 mm | - | 5/40 | 0/1500 | - | - | - | Ambient min | Ambient | Ambient Max | 0 | 700 | 900 kPa | TP-202
2 | Nitrogen |  | 21050-CSI-PR-PID-002 | Gas | MNPT | Braided Pipe (Stainless Steel) | 3/8" |  | - | 5/40 | 0/2500 | - | - | - | Ambient min | Ambient | Ambient Max | 0 | 600 | 800 kPa | TP-203
3 | Dry Compressed Air |  | 21050-CSI-PR-PID-002 | Gas | Quick Fit | Poly urethane | 3/8" | 1.6mm | - | 5/60 | 0/2500 | - | - | - | Ambient min | Ambient | 50 | 0 | 700 | 800 kPa | TP-201
Flow Through Digestor
4 | Main Water Supply |  | 21050-CSI-PR-PID-003 | Liquid | NPT Threaded Female | SS 316 | 1" |  | - | 5/40 | 0/1500 | - | - | - | Ambient min | Ambient | Ambient Max | 0 | 700 | 900 kPa | TP-204
5 | Compressed Air |  | 21050-CSI-PR-PID-003 | Gas | Quick Fit | Poly urethane | 6X4 mm | 2 mm | - | 5/60 | 0/2500 | - | - | - | Ambient min | Ambient | 50 | 0 | 700 | 800 kPa | TP-205
RDH Digestor
6 | Main Water Supply 1 |  | 21050-CSI-PR-PID-004 | Liquid | PN40 Flange | EN1.4404/316L | DN 20 |  | PN40 | 5/40 | 0/1500 | 0 LPM | 5 LPM | 15 LPM | Ambient min | Ambient | Ambient Max | 400 | 600 | 800 | TP-212 | To Process
7 | Main Water Supply 2 |  | 21050-CSI-PR-PID-004 | Liquid | PN40 Flange | EN1.4404/316L | DN 20 |  | PN40 | 5/40 | 0/1500 | 0 LPM | 20 LPM | 30 LPM | Ambient min | Ambient | Ambient Max | 300 | 500 | 600 | TP-211 | To Coolers
8 | Nitrogen |  | 21050-CSI-PR-PID-004 | Gas | BSPP Socket | EN1.4404/316L | 3/8" |  | - | 5/40 | 0/2500 | 0 NL/min | 5 NL/min | 50 NL/min | Ambient min | Ambient | Ambient Max | 1800 | 2000 | 2200 | TP-210
9 | Compressed Air |  | 21050-CSI-PR-PID-004 | Gas | BSPP Socket | EN1.4404/316L | 3/8" |  | - | 5/60 | 0/2500 | 0 NL/min | 50 NL/min | 200 NL/min | Ambient min | Ambient | Ambient Max | 600 | 650 | 800 | TP-209
10 | Steam |  | 21050-CSI-PR-PID-004 | Gas | PN40 Flange | EN1.4404/316L | DN 20 |  | PN 40 | 0/220 | Vaccum/2500 | 0 g/s | 5 g/s | 30 g/s | 180 | 190 | 200 | 1000 | 1200 | 1400 | TP-208
Wastepaper Recycler
11 | Main Water Supply |  | 21050-CSI-PR-PID-008 | Liquid | Compression | Copper | 15 mm |  | Class 2 | 5/40 | 0/1500 | 0 | 600 L/s | 700 L/s | ambient | ambient | ambient | 0 | 700 | 900 | TP-501A
12 | Main Water Supply |  | 21050-CSI-PR-PID-008 | Liquid | Compression | Copper | 15 mm |  | Class 2 | 5/40 | 0/1500 | 0 | 600 L/s | 700 L/s | ambient | ambient | ambient | 0 | 700 | 900 | TP-501B
13 | Main Water Supply |  | 21050-CSI-PR-PID-008 | Liquid | Compression | Copper | 15 mm |  | Class 2 | 5/40 | 0/1500 | 0 | 600 L/s | 700 L/s | ambient | ambient | ambient | 0 | 700 | 900 | TP-501C
14 | Hot water |  | 21050-CSI-PR-PID-008 | Liquid | Compression | Copper | 15 mm |  | Class 2 | 5/65 | 0/1500 | 0 | 190 L/h 0.05 L/s | *1.9 L/s Drainig from the 250 L | 28 | 50 | 60 | 0 | 300 | 400 | TP-502 | Heat pump has an estimsated heat capapcity of 70l/h with an 4kW (120L/h) geyser, with a 250 L tank.
LC Refiner
15 | Main Water Supply |  | 21050-CSI-PR-PID-009 | Liquid | To Atmosphere | Copper | 15 mm |  | Class 2 | 5/40 | 0/1500 | 0 | 600 L/s | 700 L/s | ambient | ambient | ambient | 0 | 700 | 900 | TP-503A
16 | Main Water Supply |  | 21050-CSI-PR-PID-009 | Liquid | To Atmosphere | Copper | 15 mm |  | Class 2 | 5/40 | 0/1500 | 0 | 600 L/s | 700 L/s | ambient | ambient | ambient | 0 | 700 | 900 | TP-503B
17 | Compressed Air |  | 21050-CSI-PR-PID-009 | Gas | Quick Fit | Poly urethane | 3/8" | 1.6mm | - | 5/60 | 0/2500 | - | - | - | Ambient min | Ambient | Ambient Max | 0 | 600 | 900 | TP-504
Valley Beater
18 | Main Water Supply |  | 21050-CSI-PR-PID-009 | Liquid | To Atmosphere | Copper | 15 mm |  | Class 2 | 5/40 | 0/1500 | 0 | 600 L/s | 700 L/s | ambient | ambient | ambient | 0 | 700 | 900 | TP-505
19 | Hot water |  | 21050-CSI-PR-PID-009 | Liquid | To Atmosphere | Copper | 15 mm |  | Class 2 | 5/65 | 0/1500 | 0 | 190 L/h 0.05 L/s | *1.9 L/s Drainig from the 250 L | 28 | 50 | 60 | 0 | 300 | 400 | TP-506
Pilot BioChar Unit
20 | Main Water Supply |  | 21050-CSI-PR-PID-006 | Liquid | BSP Thread | 304 | 1/2" |  |  | 5/40 | 0/1500 | 0 LPH |  | 20 LPH | ambient | ambient | ambient | 0 | 700 | 900 | TP-401
Gas Line
21 | Compressed Air |  | 21050-CSI-PR-PID-010 | Gas | Compression fittings | Copper | 12.7 mm (1/2") |  | Medical | 5/60 | 0/2500 | 0 |  |  | 30 | 50 | 50 | 0 | 1000 | 1600 | TP-601
22 | Nitrogen |  | 21050-CSI-PR-PID-010 | Gas | Compression fittings | Copper | 9.53 mm (3/8") |  | Medical | 5/40 | 0/2500 | 0 | - | - | ambient | ambient | ambient | 0 | 2000 | 2200 | TP-602
Liquid Line
23 | Municipal Water Supply |  | 21050-CSI-PR-PID-011 | Liquid | Compression fittings | Copper | 15/22 mm |  | Class 2 | 5/40 | 0/1500 | 0 | 600 L/s | 700 L/s | ambient | ambient | ambient | 0 | 700 | 900 | TP-801 | Various possible tie in point Flow rate is estimated from floe meter reading.
24 | Hot water |  | 21050-CSI-PR-PID-011 | Liquid | Compression fittings | Copper | 22 mm |  | Class 2 | 5/65 | 0/1500 | 0 | 190 L/h 0.05 L/s | *1.9 L/s Drainig from the 250 L | 28 | 50 | 60 | 0 | 300 | 400 | TP-802 | Heat pump has an estimsated heat capapcity of 70l/h with an 4kW (120L/h) geyser, with a 250 L tank.
Boiler
25 | Municipal Water Supply |  | 21050-CSI-PR-PID-012 | Liquid | Compression Fitting - Male BSP | Brass-Iron | 3/4" |  | Class 2 | 0/40 | 0/1500 |  |  |  | ambient | ambient | ambient | 0 | 700 | TBC
26 | Main Steam Outlet |  | 21050-CSI-PR-PID-012 | Vapour | EN 1092-2500/3 Flange | Carbon Steel | 2" | SCH 40 |  | 5/207.17 | 0/1700 |  |  |  | 120.24 | 184.13 | 207.17 | 1 00 | 1000 | 1700
27 | Safety Valve Outlet |  | 21050-CSI-PR-PID-012 | Vapour | BSP Screwed | Mild Steel | 1" | SCH 40 |  | 5/207.17 | 0/1700 |  |  |  | 0 | N/A | 207.17
28 | Blowdown Tank Drain |  | 21050-CSI-PR-PID-012 | Liquid | BSP Screwed | Mild Steel | 1 1/2"" | SCH 40 |  | 5/207.17 | 0/1700 |  |  |  | 120.24 | 184.13 | 207.17 | 1 00 | 1000 | 1700
29 | Feed Water Tank Ball Valve |  | 21050-CSI-PR-PID-012 | Liquid | Compression Fitting - Male BSP | Copper | 3/4" |  | Class 2 | 5/90 | 0/1500 |  |  |  | 0 | ambient | 40
30 | Vent on Feed Tank |  | 21050-CSI-PR-PID-012 | Liquid | BSP Screwed | Mild Steel | 2" | SCH 40 |  | 100 | Open to Atmosphere |  |  |  | Ambient | Ambient | Ambient
31 | Vent on Blowdown Tank |  | 21050-CSI-PR-PID-012 | Vapour | BSP SCrewed | Mild Steel | 2" | SCH 40 |  | 100 | Open to Atmosphere |  |  |  | <120.24 | <184.13 | <207.17
Notes | [11 empty] | References
1 | Durban water supply by law http://www.durban.gov.za/City_Services/water_sanitation/Bylaws_Tariffs/Bylaws/Pages/Water_Supply_Bylaws.aspx
2 | SANS 460 Plain-ended solid drawn copper tubes for potable water
3 |  | Design condition determine from pipeline design
4 |  | Assumed tie-in properties