## Steam Line 0.5" SW Stop Valve
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-002
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Ball Valves Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  | Prepared | Checked |  | Approved |  | Status
A |  | 2021-09-11 |  | MJ | JvdW |  | CP |  | Issued for Internal Review
Data Sheet for 1/2" Socket Weld Stop Valves
No | Rev | Section | Description |  |  |  |  | Data
1 |  | GENERAL DATA | VALVE SIZE RANGE |  | Inch (mm) |  |  | 1/2"
2 |  |  | VALVE ASME CLASS |  |  |  |  | 300 - SCH40
3 |  |  | VALVE TYPE |  |  |  |  | Stop Valve
4 |  |  | VALVE END CONFIGURATION |  |  |  |  | Socket Weld
5 |  |  | VALVE SERVICE |  |  |  |  | Steam
6 |  |  | VALVE TAG NUMBER
7 |  |  | QUANTITY |  |  |  |  | 8
8 |  |  | VALVE BORE (FULL / REDUCED) |  |  |  |  | Full Bore
9 |  |  | VALVE STANDARD |  |  |  |  | ASME B16.34 / API 608 or similar
10 |  |  | PIGGABLE |  |  |  |  | No
11 |  | DESIGN DATA | DESIGN PRESSURE (kPa) |  | barg | MAXIMUM: |  | 2500 |  |  | MINIMUM: | Full Vacuum
12 |  |  | TEMPERATURE - DESIGN (°C) |  | °C | MAXIMUM: |  | 220 |  | Note 2 | MINIMUM: | 0
13 |  |  | VALVE ACTUATOR |  |  |  |  | N/A
14 |  |  | VALVE OPERATION - MANUAL |  |  |  |  | Hand wheel
15 |  |  | VENT CONNECTION |  |  |  |  | N/A
16 |  |  | DRAIN CONNECTION |  |  |  |  | N/A
17 |  |  | PRESSURE RELIEF CONNECTION |  |  |  |  | N/A
18 |  |  | SEALANT INJECTION CONNECTION |  |  |  |  | Manufacturer's Standard
19 |  |  | SUPPORT LEGS / FEET |  |  |  |  | N/A
20 |  |  | LIFTING EYES |  |  |  |  | N/A
21 |  |  | LOCKING FACILITY |  |  |  |  | Yes
22 |  |  | SURFACE TREATMENT |  |  |  |  | 50 microns Zinc Phosphate Primer + Paint Specification for Above Ground.
23 |  | MATERIALS | BODY |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 105
24 |  |  | COVER / BONNET |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 105
25 |  |  | GLAND FLANGE |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 106
26 |  |  | BALL |  |  |  |  | Supplier to Advise
27 |  |  | DISC |  |  |  |  | Stainless Steel ASTM A276
28 |  |  | TRIM |  |  |  |  | Supplier to Advise
29 |  |  | SEALS |  |  |  |  | Supplier to Advise
30 |  |  | GASKETS |  |  |  |  | Manufacturer's Standard - Non Asbestos
31 |  |  | STEM |  |  |  |  | Supplier to Advise
32 |  |  | TRUNNION |  |  |  |  | N/A
33 |  |  | SEAT / RINGS |  |  |  |  | Supplier to Advise
34 |  |  | STEM SEAL |  |  |  |  | Viton / 316 / Graphite
35 |  |  | BOLTING |  |  |  |  | ASTM A193 B7, ASTM A194 2H
36 |  | CODES AND STANDARDS | DESIGN |  |  |  |  | API 6D
37 |  |  | DIMENSIONS |  |  |  |  | ASME B16.10
38 |  |  | THREADED DIMENSIONS |  |  |  |  | N/A
39 |  |  | FLANGE DIMENSIONS |  |  |  |  | N/A
40 |  |  | WELD END DIMENSIONS |  |  |  |  | ASME B16.11
41 |  |  | CERTIFICATION |  |  |  |  | EN 10204 3.1
42 |  |  | FIRE TEST - FIRE SAFE DESIGN |  |  |  |  | API 6FA / API 607 / BS 6755 Part 2
43 |  |  | HYDROSTATIC TEST |  |  |  |  | API 6D - No compressive end loads to be applied
44 |  | TESTING REQUIREMENTS | HYDROSTATIC SHELL TEST PRESSURE |  |  |  |  | API 598
45 |  |  | HYDROSTATIC SEAT TEST PRESSURE |  |  |  |  | API 598
46 |  |  | HIGH PRESSURE TEST |  |  |  |  | API 598
47 |  |  | ISO 5208 LEAKAGE RATE FOR SOFT SEAT |  |  |  |  | Rate A
48 |  |  | ISO 5208 LEAKAGE RATE FOR METAL SEAT |  |  |  |  | Rate D
49 |  |  | RADIOGRAPHIC TESTS |  |  |  |  | ASME B16.34 APPENDIX I
50 |  |  | ULTRASONIC TESTS |  |  |  |  | ASME B16.34 APPENDIX IV
51 |  |  | PENETRANT TESTS |  |  |  |  | ASME B16.34 APPENDIX III
52 |  |  | MAGNETIC PARTICLE TESTS |  |  |  |  | ASME B16.34 APPENDIX II
53 |  |  | MATERIAL CERTIFICATION - EN 10204 3.1.B |  |  |  |  | Required

## Steam Line 1.5" SW Stop Valve
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-002
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Ball Valves Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  | Prepared | Checked |  | Approved |  | Status
A |  | 2021-09-11 |  | MJ |  |  |  |  | Issued for Internal Review
Data Sheet for 1 1/2" Socket Weld Stop Valves
No | Rev | Section | Description |  |  |  |  | Data
1 |  | GENERAL DATA | VALVE SIZE RANGE |  | Inch (mm) |  |  | 1 1/2"
2 |  |  | VALVE ASME CLASS |  |  |  |  | 300 - SCH40
3 |  |  | VALVE TYPE |  |  |  |  | Stop Valve
4 |  |  | VALVE END CONFIGURATION |  |  |  |  | Socket Weld
5 |  |  | VALVE SERVICE |  |  |  |  | Steam
6 |  |  | VALVE TAG NUMBER |  |  |  |  | A3S or A3SS - Spirax Sarco
7 |  |  | QUANTITY |  |  |  |  | 1
8 |  |  | VALVE BORE (FULL / REDUCED) |  |  |  |  | Full Bore
9 |  |  | VALVE STANDARD |  |  |  |  | ASME B16.34 / API 608 or similar
10 |  |  | PIGGABLE |  |  |  |  | No
11 |  | DESIGN DATA | DESIGN PRESSURE (kPa) |  | barg | MAXIMUM: |  | 2500 |  |  | MINIMUM: | Full Vacuum
12 |  |  | TEMPERATURE - DESIGN (°C) |  | °C | MAXIMUM: |  | 220 |  | Note 2 | MINIMUM: | 0
13 |  |  | VALVE ACTUATOR |  |  |  |  | N/A
14 |  |  | VALVE OPERATION - MANUAL |  |  |  |  | Hand wheel
15 |  |  | VENT CONNECTION |  |  |  |  | N/A
16 |  |  | DRAIN CONNECTION |  |  |  |  | N/A
17 |  |  | PRESSURE RELIEF CONNECTION |  |  |  |  | N/A
18 |  |  | SEALANT INJECTION CONNECTION |  |  |  |  | Manufacturer's Standard
19 |  |  | SUPPORT LEGS / FEET |  |  |  |  | N/A
20 |  |  | LIFTING EYES |  |  |  |  | N/A
21 |  |  | LOCKING FACILITY |  |  |  |  | Yes
22 |  |  | SURFACE TREATMENT |  |  |  |  | 50 microns Zinc Phosphate Primer + Paint Specification for Above Ground.
23 |  | MATERIALS | BODY |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 105
24 |  |  | COVER / BONNET |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 105
25 |  |  | GLAND FLANGE |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 106
26 |  |  | BALL |  |  |  |  | Supplier to Advise
27 |  |  | DISC |  |  |  |  | Stainless Steel ASTM A276
28 |  |  | TRIM |  |  |  |  | Supplier to Advise
29 |  |  | SEALS |  |  |  |  | Supplier to Advise
30 |  |  | GASKETS |  |  |  |  | Manufacturer's Standard - Non Asbestos
31 |  |  | STEM |  |  |  |  | Supplier to Advise
32 |  |  | TRUNNION |  |  |  |  | N/A
33 |  |  | SEAT / RINGS |  |  |  |  | Supplier to Advise
34 |  |  | STEM SEAL |  |  |  |  | Viton / 316 / Graphite
35 |  |  | BOLTING |  |  |  |  | ASTM A193 B7, ASTM A194 2H
36 |  | CODES AND STANDARDS | DESIGN |  |  |  |  | API 6D
37 |  |  | DIMENSIONS |  |  |  |  | ASME B16.10
38 |  |  | THREADED DIMENSIONS |  |  |  |  | N/A
39 |  |  | FLANGE DIMENSIONS |  |  |  |  | N/A
40 |  |  | WELD END DIMENSIONS |  |  |  |  | ASME B16.11
41 |  |  | CERTIFICATION |  |  |  |  | EN 10204 3.1
42 |  |  | FIRE TEST - FIRE SAFE DESIGN |  |  |  |  | API 6FA / API 607 / BS 6755 Part 2
43 |  |  | HYDROSTATIC TEST |  |  |  |  | API 6D - No compressive end loads to be applied
44 |  | TESTING REQUIREMENTS | HYDROSTATIC SHELL TEST PRESSURE |  |  |  |  | API 598
45 |  |  | HYDROSTATIC SEAT TEST PRESSURE |  |  |  |  | API 598
46 |  |  | HIGH PRESSURE TEST |  |  |  |  | API 598
47 |  |  | ISO 5208 LEAKAGE RATE FOR SOFT SEAT |  |  |  |  | Rate A
48 |  |  | ISO 5208 LEAKAGE RATE FOR METAL SEAT |  |  |  |  | Rate D
49 |  |  | RADIOGRAPHIC TESTS |  |  |  |  | ASME B16.34 APPENDIX I
50 |  |  | ULTRASONIC TESTS |  |  |  |  | ASME B16.34 APPENDIX IV
51 |  |  | PENETRANT TESTS |  |  |  |  | ASME B16.34 APPENDIX III
52 |  |  | MAGNETIC PARTICLE TESTS |  |  |  |  | ASME B16.34 APPENDIX II
53 |  |  | MATERIAL CERTIFICATION - EN 10204 3.1.B |  |  |  |  | Required