## 1.5" Steam Air Vent
Project |  | BIDF Expansion |  |  |  |  | Page 1 of 1
Document No. |  | 21050-CSI-ME-DAS-004
Location |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Air Vents - Steam boiler
Revision Status
Rev No. |  | Date | Prepared By | Revised Sheet | Revision | Approvals
[6 empty] | Checked By | Approved By
A |  | 2020-02-11 | MJ | All | Issued for Internal Review
1 | Description |  |  | Thermostatic Air Vent
2 | Reference P&ID |  |  | 19088-PS2-PR-PID-012
3 | Item Number:
4 | Quantity: |  |  | 1
5 | Service: |  |  | Vent Excess Air in Steam Line
6 | Fluid: |  |  | Steam |  | Water
7 | Standard type: |  |  | European Pressure Equipment Directive 97/23/EC
8 | Flowrate: |  | min: | 0 |  |  |  | kg/hr
|  |  | Operating | 108 |  |  |  | kg/hr
|  |  | max: | 200 |  |  |  | kg/hr
|  |  | design: | 300 |  |  |  | kg/hr
9 | Temperature: |  | min: | 0 |  |  |  | oC
|  |  | max: | 190 |  |  |  | oC
|  |  | design (min/max): | 220 |  |  |  | oC
10 | Pressure: |  | min: | 100 |  |  |  | kPa
|  |  | max: | 1700 |  |  |  | kPa
|  |  | design: | 1850 |  |  |  | kPa
11 | Class |  |  | 300
12 | Connection Type: |  | inlet: | 1.5" Socket Weld Ends - ASME SCH 40 Pipe
|  |  | outlet: | 1.5" Socket Weld Ends - ASME SCH 40 Pipe
16 | Corrosion Allowance: |  |  | 1 |  |  |  | mm
18 | Material: |  | Cover: | Carbon Steel / Alloy Steel - Weldable Carbon Steel to ASTM A106 Gr B
|  |  | Locking Nut: | VTC
|  |  | Thermostatic Element: | VTC
|  |  | Strainer Screen: | VTC
|  |  | Valve Seat: | VTC
|  |  | Valve Seat Gasket: | VTC
|  |  | Valve: | VTC
|  |  | Spring: | VTC
|  |  | Body: | Carbon Steel / Alloy Steel - Weldable Carbon Steel to ASTM A106 Gr B
|  |  | Bolting: | ASTM A193 Gr B7
|  |  | Seat Insert: | VTC
General Requirements
21 | 1 - Weld Quality Requirements in accordance with ISO 3834
22 | 2- Test Report ans Material Certification Required
23 | 3 - Seals and Gaskets to to be compatible with Steam