## Elect Biopharm
4021 | CSIR - SMALL MOLECULE AND BIOPHARM FACILITY
SCIENTIA CAMPUS PRETORIA
Electrical Installation - Biopharm Lab
| 2022-09-09 |  | REV 3
ITEM | DESCRIPTION | UNIT | QTY | MATERIAL | LABOUR | TOTAL
BILL NO.1 : PRELIMINARY AND GENERAL COSTS
1.1 | SITE ESTABLISHMENT
| Camp and fencing | sum | 1
| Office | sum | 1
| Office Equipment | sum | 1
| Store | sum | 1
| Workshop | sum | 1
| Other | sum | 1
1.2 | ADMINISTRATIVE
| Site personnel | sum | 1
| Supervisory staff | sum | 1
| Guards | sum | 1
| Transport | sum | 1
| Insurance | sum | 1
| Cost of Guarantee | sum | 1
| Financing of Retention | sum | 1
| Running costs e.g. telephone, electricity,cleaning services,printing, stationery, etc | sum | 1
1.3 | GENERAL COSTS
Allow an amount if required for expenses incurred
| to tender. | sum | 1
| Loading and off loading of material and equipment | sum | 1
| Setting out of Works. | sum | 1
| Cleaning of site upon completion of Contract. | sum | 1
| Critical Path/Schedule. | sum | 1
| Marking up "As Built" drawings | sum | 1
| Issuing Cadded "As Built" drawings on completion | sum | 1
| Test and commissioning of complete Works. | sum | 1
| Inspection and handing over. | sum | 1
| Certificate of Compliance | sum | 1
| Maintenance manuals | ea | 4
| TOTAL BILL NO 1 |  |  |  |  | 0
A | INSTALLATION - GENERAL
The following shall apply to all material and equipment supplied and installed on site and shall conform to specifications contained in the technical specification of this document.
A.1 | WIRING CHANNEL
Galvanised metal channel complete with covers fixed at intervals not exceeding 1.5m. Channel to be complete with all splices, bends, T-pieces, ends etc.
A.2 | CONDUITS & DRAW BOXES
Conduits cast in concrete, chased into brickwork,fixed in partitioning, roof spaces, surface on concrete or brickwork to be complete with saddles, couplings and terminations to drawboxes. Draw boxes to be galvanised type. All cutting and terminations to be included.
A.3 | LIGHT FITTINGS
Take delivery of, store, install and connect all light fittings complete with lamps, gear, etc. as specified and indicated on the drawings. All fluorescent lamps to be Colour 840 unless indicated otherwise.
A.4 | CONDUCTORS
SABS approved PVC insulated copper conductors drawn into conduit, installed in wiring trunking or power skirting.
A.5 | SOCKET OUTLETS
16A, 3-pin switched socket outlets flush mounted in drawboxes complete with cover plates shall be of the "Crabtree"or "Clipsal" range which fit into standard outlet boxes dedicated outlets shall have a red cover plate.Floor boxes shall be of the "Cabstrut" range. or similar
A.6 | LIGHT SWITCHES
16A light switch flush mounted in draw boxes or power skirting complete with cover plates shall be of the "Crabtree" or "Clipsal" range which fit into standard outlet boxes.
A.7 | DISTRIBUTION BOARDS
Supply & Install Distribution Boards complete as in accordance with the specification and drawings
A.8 | ISOLATORS
Isolators surface/flush mounted in 100 x 100mm x 50mm draw boxes complete with coverplate as specified and indicated on drawings. All isolators installed externally shall be in weather proof enclosures
A.9 | LOW VOLTAGE CABLES
600/1000V PVC/SWA/PVC Cables with copper conductors to SABS 1507 fixed vertically or horizontally on cable trays in accordance with the specification and drawings. All fixings to be included.
A.10 | TERMINATIONS
Termination of LV cable to be as specified including connection of conductors, cable lugs, captive cone glands, shrouds, etc. for the relevant cable sizes.
BILL NO 2:
Small Power & Lighting - BioPharm Facility
NOTE:
All clean room penetrations must be sealed with anti-bacterial silicone
3.1 | LV CABLES
Supply and installation of the following PVC armoured SWA copper cables to SANS 1507, installed on cable Trays vertically and horizontally.
| 95mm² x 4-core | m | 20
| 10mm² x 4-core | m | 50
3.2 | TERMINATIONS
Termination of LV cable as specified including connection of conductors, cable lugs, captive glands, shrouds, etc. for the following cable sizes
| 95mm² x 4-core | ea | 2
| 10mm² x 4-core | ea | 2
3.3 | EARTHING
Supply and install the following bare copper earth conductors
| 50mm2 bare earth conductor | m | 20
| 6mm² bare earth conductor | m | 50
3.4 | TERMINATION OF EARTH CONDUCTORS
| 50mm² bare earth conductor | ea | 2
| 10mm² bare earth conductor | ea | 2
3.5 | DISTRIBUTION BOARDS & SWITCH GEAR
Provide an infra red scan to check all terminations in the distribution board and replace missing blank circuit breaker covers. Ensure that all labelling is complete and legend cards are provided and updated. Ensure that all warning signs are provided. Test the earthing of DB. Ensure that cover plates are properly secured. Provide a Certificate of compliance for the distribution board in accordance with SANS 10142.
LIST OF DISTRIBUTION BOARDS
| SDB - BPG (New) | ea | 1
| SDB - BPF (New) | ea | 1
3.6 | STRIP OUT EXISTING ELECTRICAL SERVICES
| Strip out existing electrical services BioPharm facility 327m² | sum | 1
3.7 | UPS
| Suply and install an Eaton 20 kVA UPS and associated batteries for 10 min back-up | sum | 1
3.8 | Cable Trays
Heavy Duty, hot dipped galvanised Return Flange cable tray (RFHD) complete with splices, nuts, bolts and washers fixed horizontally on hangers or vertically up walls and risers.
| 150 mm wide x 50 mm HD cable ladder | m | 60
| Horizontal bends | ea | 3
| Tee Piece | ea | 1
| External Elbow | ea | 2
| Cable ladder fixings | ea | 40
| 200mm Wire Mesh tray | m | 92
| Horizontal Bends | ea | 5
| Vertical Bend | ea | 2
| Tee pieces | ea | 10
| Cable Tray Hanger | ea | 62
| 100mm Wire Mesh tray | m | 92
| Horizontal Bends | ea | 5
| Vertical Bend | ea | 2
| Tee pieces | ea | 10
| Cable Tray Hanger | ea | 62
| 100mm Perforated tray | m | 0
| Horizontal Bends | ea | 0
| Vertical Bend | ea | 0
| Tee pieces | ea | 0
| Perforated Tray fixings | ea | 0
3.9 | Supply and Installation of the Following Circuit Breakers
| 15Amp Circuit Breaker - 5kA | ea | 1
| 20Amp Circuit Breaker - 5kA | ea | 0
| 40Amp Circuit Breaker - 5kA | ea | 0
| 63Amp Trip Pole Circuit Breaker - 10kA | ea | 0
| 80Amp Trip Pole Circuit Breaker - 10kA | ea | 0
| 160Amp Trip Pole Circuit Breaker - 15kA | ea | 0
| 250Amp Trip Pole Circuit Breaker - 15kA | ea | 0
| 60Amp Earth Leakage Circuit Breaker rate at 30mA | ea | 0
| 40 Amp 3 pole AC3 Duty Contactor | ea | 0
3.1 | WIRING CHANNEL
Galvanised steel channel complete with covers fixed at intervals not exceeding 1.5m. Channel to be complete with all splices, bends, T-pieces, ends etc.
(Type OL or similar manufactured channel).
Supply & Install
| P9000 + Cover - suspended / in celing void for electrical services | m | 132
| P9000 - Tee Piece | ea | 11
| P9000 Horizontal Bend | ea | 5
| P9000 Vertical Bend | ea | 1
| End Caps | ea | 2
| Cross Piece | ea | 1
| Hangers | ea | 62
| P8000 + Cover - suspended / in celing void for electrical services | m | 132
| P8000 - Tee Piece | ea | 11
| P8000 Horizontal Bend | ea | 5
| P8000 Vertical Bend | ea | 1
| Cross Pieces | ea | 1
| End Caps | ea | 2
| Hangers | ea | 62
| P2000 + Cover - suspended / in celing void for electrical services | m | 132
| P2000 - Tee Piece | ea | 11
| P2000 Horizontal Bend | ea | 5
| P2000 Vertical Bend | ea | 1
| Cross Pieces | ea | 11
| Hangers | ea | 62
SMALL POWER INSTALLATION
3.11 | Conduit
Supply and Install
PVC conduit installed chased in walls and in open roof spaces in the following sizes
| 20mm PVC | m | 196
| 25mm PVC | m | 0
| 32mm PVC | m | 0
| 50mm PVC | m | 0
Bosal conduit, installed chased in walls, surface mounted and in open roof spaces on the following sizes
| 25mm Bosal | m | 100
| 25mm metal Sprague (500mm) | m | 0
| 25mm Bosal Threaded Dome Lid | ea | 0
3.12 | Outlet Boxes
Supply and Install
Galvanised steel draw and outlet boxes installed surface, in ceiling spaces or chased into brickwalls, in the following sizes
| 100mm x 100mm x 50mm deep | ea | 70
| 100mm x 50mm x 50mm deep | ea | 2
| 100mm x 75mm x 50mm deep | ea | 0
| 60mm round , 2-way | ea | 12
| Wonderboxes with cover plate | ea | 1
3.13 | SOCKET OUTLETS
Supply and Install
| 16A SSO - Flush in draw box | ea | 17
| 16A Double SSO - Flush in draw box | ea | 0
| 16A SSO + 2 x Switched ZA sockets | ea | 20
| 16A SSO with half-round earth pin and red face plate in draw box | ea | 1
| 16A Double SSO with half-round earth pin and red face plate in draw box | ea | 0
| 16A SSO - Flush in powerskirting normal | ea | 0
| 16A SSO - Flush in powerskirting dedicated | ea | 20
| ZA Socket outlet in power skirting | ea | 14
| 16A SSO - Flush in powerskirting dedicated | ea | 9
| RJ45 data outlet in power skirting | ea | 1
| RJ45 data outlet in power skirting | ea | 0
| RJ45 data outlet flush in drawbox | ea | 0
| RJ45 data outlet in power pole enclosure | ea | 0
| 16A SSO - Dedicated mounted in power pole enclosure with face plate | ea | 6
| ZA Socket outlet in power pole with cover plate | ea | 6
| Data outlet RJ45 in power pole with cover plate | ea | 6
| 16A SSO - In weatherproof york box built in to the wall (for garden equipment) | ea | 0
| Satelite television outlets with F-connector in 100 x 100 drawbox flush mounted | ea | 0
| RJ11 Telephone outlets in power skirting | ea | 0
| RJ11 Telephone outlets in drawbox with cover plate | ea | 0
| RJ11 Telephone outlets in power pole enclosure | ea | 0
| Stainless Steel Power Pole c/w baseplate and ceiling fixings | ea | 3
3.14 | ISOLATORS
Isolators mounted complete with backbox on 100x100 outlet boxes or power skirting.
Supply & Install the following sizes:
| 20A 2-pole | ea | 9
| 32A 2-pole | ea | 0
| 60A 2-pole | ea | 0
| 20A 3-pole | ea | 0
| 32A 3-pole | ea | 0
| 40A 3-pole | ea | 1
| 63A 3-pole | ea | 0
| 80A 3-pole | ea | 0
| 125A 3-pole | ea | 0
| 20A 2-pole IP65 | ea | 0
| 20A 3-pole IP65 (Welding socket) | ea | 2
| 32A 3-pole IP65 (Welding socket) | ea | 0
| 63A 3-pole IP65 (Welding socket) | ea | 1
3.15 | CONDUCTORS
Supply and Install
| 2.5mm² stranded PVC insulated copper conductors | m | 3750
| 4mm² stranded PVC insulated with copper conductors | m | 25
| 6mm² stranded PVCinsulated with copper conductors | m | 0
| 10mm² stranded PVC insulated with copper conductors | m | 0
| 16mm² stranded PVC insulated with copper conductors | m | 0
| 25mm² stranded PVC insulated with copper conductors | m | 0
| 35mm² stranded PVC insulated with copper conductors (rate only) | m | 0
3.16 | INNOVATIVE WIRING
Supply and Install
| 2.5mm² Twin & Earth | m | 0
| 4.0 mm² Twin & Earth | m | 0
| 6mm² x 4 core surfix | m | 0
3.17 | POWER SKIRTING
Supply and Install
| 2-Compartment, 2-Cover Steel powder coated power skirting | m | 54
| Cover only for power skirting | m | 54
| Corner - 90deg. Internal | ea | 16
| Corner - 90deg. External | ea | 7
| End Caps | ea | 10
| Horizontal bend | ea | 0
3.18 | LIGHTING INSTALLATION
Conduit
Supply and Install
PVC conduit, installed chased in walls and in open roof spaces in the following sizes
| 20mm | m | 140
| 25mm | m | 0
Bosal conduit, installed chased in walls, surface mounted and in open roof spaces on the following sizes
| 20mm Bosal | m | 100
| 25mm Bosal | m | 0
| 25mm metal Sprague | m | 0
| 25mm Bosal Threaded Dome Lid | ea | 0
3.19 | Outlet Boxes
Supply and Install
Galvanised steel draw and outlet boxes installed surface , Brass bushes & locknuts in ceiling spaces or chased into Brickwalls, in the following sizes
| 100mm x 50mm x 50mm deep | ea | 13
| 60mm round , 1,2 or 3-way | ea | 2
| 100mm x 100mm x 50mm deep | ea | 2
3.2 | Light Switches(Complete with Cover Plates)
Supply and Install
| 16A 1 - Lever ; 1 - Way switch - flush in draw box | ea | 9
| 16A 1 - Way ; dimmer switch - flush in draw box | ea | 0
| 16A 1- Lever, 2-Way switch - flush in draw box | ea | 0
| 16A 1- Lever, Intermediate switch - flush in draw box | ea | 0
| 16A 2 - Lever ; 1 - Way switch - flush in draw box | ea | 2
| 16A 2 - Lever, 2-Way switch - flush in draw box | ea | 0
| 16A 3 - Lever ; 1 - Way switch - flush in draw box | ea | 0
| 16A 3 - Lever ; 2 - Way switch - flush in draw box | ea | 0
| 5Amp unswitched socket outlets complete with ROUND Box | ea | 136
3.21 | LIGHT FITTINGS
Supply,take delivery, store, install the following light fittings with lamps & including the necessary supports etc. As specified and indicated on drawings. All fluorescent lamps to be either Osram or Phillips lamps. Colour 840. LED lamps to be neutral white unless otherwise stated. All fluorescent light fittings to have electronic control ballast.
TYPE | Supply & Install
A | 600 x 600 Recessed panel luminiare white 30W LED luminaire with opal diffuser. Similar and equal to Province/RubiconTHEIA 4000K c/w 3m lead and 5A plugtop | ea | 69
Ae | Same as Type A but with 1 hour emergency control gear and 2x 3m lead with 5A plugtop | ea | 5
B | 600 x 600 Recessed panel luminiare white 40W LED luminaire with opal diffuser. Similar and equal to Province/Rubicon HELLAS 4000K c/w 3m lead and 5A plugtop | ea | 24
Be | Same as Type B but with 1 hour emergency control gear c/w 2 x 3m lead and 5A plugtop | ea | 2
C | Explosion proof luminiare Class 1 Div 1 Similar and equal to Province/Rubicon CHADD 67W 4000K |  | 0
D | Surface mounted vapour proof luminiare Province/Rubicon Metropolis 47W 4000K | ea | 12
De | Same as type D but with emergency 1 hr control gear. | ea | 2
E | Recessed downlight Province/Rubicon MARIA 80 10W 4000K c/w 3m lead and 5 A plugtop. | ea | 14
F | Recessed downlight Province/Rubicon MARIA 110 15W 4000K c/w 3m lead and 5 A plugtop. | ea | 0
G | 2.8m LED Strip light LF 45 600 lm/m in 45 deg aluminium channel. c/w LED 60W Driver | ea | 2
Ge | Same as Type G but with emergency control gear 1Hr. | ea | 0
| Photo cell. Similar and equal to Major Tech DNS6 | ea | 0
3.22 | CONDUCTORS
| 2.5mm² stranded insulated PVC with copper conductors | m | 1540
| 4mm² stranded insulated PVC with copper conductors | m | 0
| 2.5mm² Twin & Earth | m | 0
3.23 | SENSORS
| Ceiling mounted 360deg occupancy sensors 1000W Major Tech PIR 45 | ea | 0
| TOTAL FOR BILL NO 2 |  |  |  |  | 0
CSIR - BIOPHARM FACILITY - Summary
| Bill no. 1 Preliminary & General |  |  |  |  | 0
| Bill no. 2 Small Power & Lighting - BioPharm Facility |  |  |  |  | 0
| Provisional Amount for power supply to HVAC & Ventilation |  |  |  |  | 60000
Sub Total
TOTAL CARRIED FORWARD TO MAIN CONTRACTORS BILL OF QUANTITIES (excl VAT)

## Elect SMF
4021 | CSIR - SMALL MOLECULE AND BIOPHARM FACILITY
SCIENTIA CAMPUS PRETORIA
Electrical Installation - Small Molecule Facility
| 2022-09-09 |  | REV 3
ITEM | DESCRIPTION | UNIT | QTY | MATERIAL | LABOUR | TOTAL
BILL NO.1 : PRELIMINARY AND GENERAL COSTS
1.1 | SITE ESTABLISHMENT
| Camp and fencing | sum | 1
| Office | sum | 1
| Office Equipment | sum | 1
| Store | sum | 1
| Workshop | sum | 1
| Other | sum | 1
1.2 | ADMINISTRATIVE
| Site personnel | sum | 1
| Supervisory staff | sum | 1
| Guards | sum | 1
| Transport | sum | 1
| Insurance | sum | 1
| Cost of Guarantee | sum | 1
| Financing of Retention | sum | 1
| Running costs e.g. telephone, electricity,cleaning services,printing, stationery, etc | sum | 1
1.3 | GENERAL COSTS
Allow an amount if required for expenses incurred
| to tender. | sum | 1
| Loading and off loading of material and equipment | sum | 1
| Setting out of Works. | sum | 1
| Cleaning of site upon completion of Contract. | sum | 1
| Critical Path/Schedule. | sum | 1
| Marking up "As Built" drawings | sum | 1
| Issuing Cadded "As Built" drawings on completion | sum | 1
| Test and commissioning of complete Works. | sum | 1
| Inspection and handing over. | sum | 1
| Certificate of Compliance | sum | 1
| Maintenance manuals | ea | 4
| TOTAL BILL NO 1 |  |  |  |  | 0
A | INSTALLATION - GENERAL
The following shall apply to all material and equipment supplied and installed on site and shall conform to specifications contained in the technical specification of this document.
A.1 | WIRING CHANNEL
Galvanised metal channel complete with covers fixed at intervals not exceeding 1.5m. Channel to be complete with all splices, bends, T-pieces, ends etc.
A.2 | CONDUITS & DRAW BOXES
Conduits cast in concrete, chased into brickwork,fixed in partitioning, roof spaces, surface on concrete or brickwork to be complete with saddles, couplings and terminations to drawboxes. Draw boxes to be galvanised type. All cutting and terminations to be included.
A.3 | LIGHT FITTINGS
Take delivery of, store, install and connect all light fittings complete with lamps, gear, etc. as specified and indicated on the drawings. All fluorescent lamps to be Colour 840 unless indicated otherwise.
A.4 | CONDUCTORS
SABS approved PVC insulated copper conductors drawn into conduit, installed in wiring trunking or power skirting.
A.5 | SOCKET OUTLETS
16A, 3-pin switched socket outlets flush mounted in drawboxes complete with cover plates shall be of the "Crabtree"or "Clipsal" range which fit into standard outlet boxes dedicated outlets shall have a red cover plate.Floor boxes shall be of the "Cabstrut" range. or similar
A.6 | LIGHT SWITCHES
16A light switch flush mounted in draw boxes or power skirting complete with cover plates shall be of the "Crabtree" or "Clipsal" range which fit into standard outlet boxes.
A.7 | DISTRIBUTION BOARDS
Supply & Install Distribution Boards complete as in accordance with the specification and drawings
A.8 | ISOLATORS
Isolators surface/flush mounted in 100 x 100mm x 50mm draw boxes complete with coverplate as specified and indicated on drawings. All isolators installed externally shall be in weather proof enclosures
A.9 | LOW VOLTAGE CABLES
600/1000V PVC/SWA/PVC Cables with copper conductors to SABS 1507 fixed vertically or horizontally on cable trays in accordance with the specification and drawings. All fixings to be included.
A.10 | TERMINATIONS
Termination of LV cable to be as specified including connection of conductors, cable lugs, captive cone glands, shrouds, etc. for the relevant cable sizes.
BILL NO 2: Small Molecule Facility
Small Power & Lighting
2.1 | LV cables
Supply and installation of the following PVC armoured SWA copper cables to SANS 1507, installed on cable Trays vertically and horizontally.
| 25mm² x 4-core | m | 74
2.2 | TERMINATIONS
Termination of LV cable as specified including connection of conductors, cable lugs, captive glands, shrouds, etc. for the following cable sizes
| 25mm² x 4-core | ea | 2
2.3 | EARTHING
Supply and install the following bare copper earth conductors
| 16mm² bare earth conductor | m | 74
2.4 | TERMINATION OF EARTH CONDUCTORS
| 16mm² bare earth conductor | ea | 2
2.5 | DISTRIBUTION BOARDS & SWITCH GEAR
Provide an infra red scan to check all terminations in the distribution board and replace missing blank circuit breaker covers. Ensure that all labelling is complete and legend cards are provided and updated. Ensure that all warning signs are provided. Test the earthing of DB. Ensure that cover plates are properly secured. Provide a Certificate of compliance for the distribution board in accordance with SANS 10142.
LIST OF DISTRIBUTION BOARDS
| SDB - 13 (Retrofit as per single line diagram) | ea | 1
| SDB - DB UPS (New) | ea | 1
| SDB on First Floor small molecule (alterations) | ea | 1
2.6 | STRIP OUT EXISTING ELECTRICAL SERVICES
| Strip out existing electrical services small molecule facility 507m² | sum | 1
2.7 | UPS
| Suply and install an Eaton 40 kVA UPS and associated batteries for 10 min back-up | sum | 1
2.8 | Cable Trays
Heavy Duty, hot dipped galvanised Return Flange cable tray (RFHD) complete with splices, nuts, bolts and washers fixed horizontally on hangers or vertically up walls and risers.
| 100 mm wide x 50 mm HD cable ladder | m | 5
| Horizontal bends | ea | 1
| Tee Piece | ea | 0
| External Elbow | ea | 1
| Cable ladder fixings | ea | 5
| 200mm Wire Mesh tray | m | 145
| Horizontal Bends | ea | 8
| Vertical Bend | ea | 1
| Cross pieces |  | 8
| Tee pieces | ea | 8
| Cable Tray Hanger | ea | 98
| 100mm Wire Mesh tray | m | 145
| Horizontal Bends | ea | 8
| Vertical Bend | ea | 1
| Cross pieces | ea | 8
| Tee pieces | ea | 8
| Cable Tray Hanger | ea | 98
| 200mm Perforated tray | m | 10
| Horizontal Bends | ea | 1
| Vertical Bend | ea | 1
| Tee pieces | ea | 0
| Perforated Tray fixings | ea | 10 |  |  |  | 0
| 100mm Perforated tray | m | 70
| Horizontal Bends | ea | 4
| Vertical Bend | ea | 2
| Tee pieces | ea | 0
| Perforated Tray fixings | ea | 47
2.9 | Supply and Installation of the Following Circuit Breakers
| 15Amp Circuit Breaker - 5kA | ea | 0
| 20Amp Circuit Breaker - 5kA | ea | 0
| 40Amp Circuit Breaker - 5kA | ea | 0
| 63Amp Trip Pole Circuit Breaker - 5kA | ea | 1
| 80Amp Trip Pole Circuit Breaker - 10kA | ea | 0
| 160Amp Trip Pole Circuit Breaker - 15kA | ea | 0
| 60Amp Earth Leakage Circuit Breaker rate at 30mA | ea | 0
| 40 Amp 3 pole AC3 Duty Contactor | ea | 0
2.1 | WIRING CHANNEL
Galvanised steel channel complete with covers fixed at intervals not exceeding 1.5m. Channel to be complete with all splices, bends, T-pieces, ends etc.
(Type OL or similar manufactured channel).
Supply & Install
| P9000 + Cover - suspended / in celing void for electrical services | m | 145
| P9000 - Tee Piece | ea | 8
| P9000 Horizontal Bend | ea | 1
| P9000 Vertical Bend | ea | 0
| P9000 Cross Piece | ea | 8
| End Caps | ea | 0
| Hangers | ea | 98
| P8000 + Cover - suspended / in celing void for electrical services | m | 145
| P8000 - Tee Piece | ea | 8
| P8000 Horizontal Bend | ea | 1
| P8000 Vertical Bend | ea | 1
| Cross Pieces | ea | 8
| End Caps | ea | 0
| Hangers | ea | 98
| P2000 + Cover - suspended / in celing void for electrical services | m | 145
| P2000 - Tee Piece | ea | 8
| P2000 Horizontal Bend | ea | 4
| P2000 Vertical Bend | ea | 1
| P2000 Cross piece | ea | 8
| Hangers | ea | 98
0
SMALL POWER INSTALLATION
2.11 | Conduit
Supply and Install
PVC conduit installed chased in walls and in open roof spaces in the following sizes
| 20mm PVC | m | 215
| 25mm PVC | m | 10
| 32mm PVC | m | 0
| 50mm PVC | m | 0
Bosal conduit, installed chased in walls, surface mounted and in open roof spaces on the following sizes
| 25mm Bosal | m | 100
| 25mm metal Sprague (500mm) | m | 0
| 25mm Bosal Threaded Dome Lid | ea | 0
2.12 | Outlet Boxes
Supply and Install
Galvanised steel draw and outlet boxes installed surface, in ceiling spaces or chased into brickwalls, in the following sizes
| 100mm x 100mm x 50mm deep | ea | 84
| 100mm x 50mm x 50mm deep | ea | 0
| 100mm x 75mm x 50mm deep | ea | 0
| 60mm round , 2-way | ea | 12
| Wonderboxes with cover plate | ea | 0
2.13 | SOCKET OUTLETS
Supply and Install
| 16A SSO - Flush in draw box | ea | 0
| 16A Double SSO - Flush in draw box | ea | 0
| 16A SSO + 2 x Switched ZA sockets | ea | 41
| 16A SSO with half-round earth pin and red face plate in draw box | ea | 18
| 16A Double SSO with half-round earth pin and red face plate in draw box | ea | 0
| 16A SSO - Flush in powerskirting normal | ea | 30
| ZA Socket outlet in power skirting | ea | 14
| 16A SSO - Flush in powerskirting dedicated | ea | 9
| RJ45 data outlet in power skirting | ea | 1
| RJ45 data outlet flush in drawbox | ea | 1
| RJ45 data outlet in power pole enclosure | ea | 0
| 16A SSO - Normal mounted in power pole enclosure with face plate | ea | 0
| 16A SSO - ZA socket mounted in power pole enclosure with face plate | ea | 0
| 16A SSO - Dedicated mounted in power pole enclosure with face plate | ea | 0
| Data outlet mounted in power pole enclosure with face plate | ea | 0
| 16A SSO - In weatherproof york box built in to the wall (for garden equipment) | ea | 0
| Satelite television outlets with F-connector in 100 x 100 drawbox flush mounted | ea | 0
| RJ11 Telephone outlets in power skirting | ea | 0
| RJ11 Telephone outlets in drawbox with cover plate | ea | 0
| RJ11 Telephone outlets in power pole enclosure | ea | 0
| UK Socket to South African socket adaptor | ea | 20
2.14 | ISOLATORS
Isolators mounted complete with backbox on 100x100 outlet boxes or power skirting.
Supply & Install the following sizes:
| 20A 2-pole | ea | 15
| 32A 2-pole | ea | 0
| 60A 2-pole | ea | 0
| 20A 3-pole | ea | 1
| 32A 3-pole | ea | 3
| 40A 3-pole | ea | 0
| 63A 3-pole | ea | 0
| 80A 3-pole | ea | 0
| 125A 3-pole | ea | 0
| 20A 2-pole IP65 | ea | 0
| 20A 3-pole IP65 (Welding socket) | ea | 1
| 32A 3-pole IP65 (Welding socket) | ea | 0
| 63A 3-pole IP65 (Welding socket) | ea | 1
2.15 | CONDUCTORS
Supply and Install
| 2.5mm² stranded PVC insulated copper conductors | m | 5560
| 4mm² stranded PVC insulated with copper conductors | m | 20
| 6mm² stranded PVCinsulated with copper conductors | m | 0
| 10mm² stranded PVC insulated with copper conductors | m | 0
| 16mm² stranded PVC insulated with copper conductors | m | 0
| 25mm² stranded PVC insulated with copper conductors | m | 0
| 35mm² stranded PVC insulated with copper conductors (rate only) | m | 0
2.16 | INNOVATIVE WIRING
Supply and Install
| 2.5mm² Twin & Earth | m | 0
| 4.0 mm² Twin & Earth | m | 0
| 6mm² x 4 core surfix | m | 0
2.17 | POWER SKIRTING
Supply and Install
| 2-Compartment, 2-Cover Steel powder coated power skirting | m | 44
| Cover only for power skirting | m | 44
| Corner - 90deg. Internal | ea | 3
| Corner - 90deg. External | ea | 1
| End Caps | ea | 14
| Horizontal bend | ea | 0
0
2.18 | LIGHTING INSTALLATION
Conduit
Supply and Install
PVC conduit, installed chased in walls and in open roof spaces in the following sizes
| 20mm | m | 65
| 25mm | m | 0
Bosal conduit, installed chased in walls, surface mounted and in open roof spaces on the following sizes
| 20mm Bosal | m | 100
| 25mm Bosal | m | 0
| 25mm metal Sprague | m | 0
| 25mm Bosal Threaded Dome Lid | ea | 0
2.19 | Outlet Boxes
Supply and Install
Galvanised steel draw and outlet boxes installed surface , Brass bushes & locknuts in ceiling spaces or chased into Brickwalls, in the following sizes
| 100mm x 50mm x 50mm deep | ea | 15
| 60mm round , 1,2 or 3-way | ea | 4
| 100mm x 100mm x 50mm deep | ea | 0
2.2 | Light Switches(Complete with Cover Plates)
Supply and Install
| 16A 1 - Lever ; 1 - Way switch - flush in draw box | ea | 13
| 16A 1 - Way ; dimmer switch - flush in draw box | ea | 0
| 16A 1- Lever, 2-Way switch - flush in draw box | ea | 0
| 16A 1- Lever, Intermediate switch - flush in draw box | ea | 0
| 16A 2 - Lever ; 1 - Way switch - flush in draw box | ea | 0
| 16A 2 - Lever, 2-Way switch - flush in draw box | ea | 0
| 16A 3 - Lever ; 1 - Way switch - flush in draw box | ea | 0
| 16A 3 - Lever ; 2 - Way switch - flush in draw box | ea | 0
| 5Amp unswitched socket outlets complete with ROUND Box mounted to trunking | ea | 135
2.21 | LIGHT FITTINGS
Supply,take delivery, store, install the following light fittings with lamps & including the necessary supports etc. As specified and indicated on drawings. All luminiares shall be equipped with LED lamps 4000K unless otherwise specified.
TYPE | Supply & Install
A | 600 x 600 Recessed panel luminiare white 30W LED luminaire with opal diffuser. Similar and equal to Province/RubiconTHEIA 4000K c/w 3m lead and 5A plugtop | ea | 83
Ae | Same as Type A but with 1 hour emergency control gear and 2x 3m lead with 5A plugtop | ea | 10
B | 600 x 600 Recessed panel luminiare white 40W LED luminaire with opal diffuser. Similar and equal to Province/Rubicon HELLAS 4000K c/w 3m lead and 5A plugtop | ea | 0
Be | Same as Type B but with 1 hour emergency control gear c/w 2 x 3m lead and 5A plugtop | ea | 0
C | Explosion proof luminiare Class 1 Div 1 Similar and equal to Province/Rubicon CHADD 67W 4000K |  | 6
D | Surface mounted vapour proof luminiare Province/Rubicon Metropolis 47W 4000K | ea | 19
De | Same as type D but with emergency 1 hr control gear. | ea | 3
E | Recessed downlight Province/Rubicon MARIA 80 10W 4000K c/w 3m lead and 5 A plugtop. | ea | 0
F | Recessed downlight Province/Rubicon MARIA 110 15W 4000K c/w 3m lead and 5 A plugtop. | ea | 0
| Photo cell. Similar and equal to Major Tech DNS6 | ea | 0
2.22 | CONDUCTORS
| 2.5mm² stranded insulated PVC with copper conductors | m | 1992
| 4mm² stranded insulated PVC with copper conductors | m | 0
| 2.5mm² Twin & Earth | m | 0
2.23 | SENSORS
| Ceiling mounted 360deg occupancy sensors 1000W Major Tech PIR 45 | ea | 0
| TOTAL FOR BILL NO 2 |  |  |  |  | 0
CSIR - SMALL MOLECULE AND BIOPHARM FACILITY - Summary
| Bill no. 1 Preliminary & General |  |  |  |  | 0
| Bill no. 2 Small Power & Lighting - Small Molecule Facility |  |  |  |  | 0
| Provisional Amount for Earthing of Reactor Bay |  |  |  |  | 8000
| Provisional Amount for power supply to HVAC & Ventilation |  |  |  |  | 180000
Sub Total
TOTAL CARRIED FORWARD TO MAIN CONTRACTORS BILL OF QUANTITIES (excl VAT)

## 5.4 Sum
Electrical Bills of Quantities
Bill No |  |  |  | Amount
5.4 |  | Electrical Bills of Quantities | R
|  | Main Contractors percentage for all mark-ups, attendance, etc on specialist domestic contractor | R
0
|  | Carried Forward To Section 5.10 : Final Summary | R |  |  | 0 | 0
CSIR Future PHARMA Facility
Section 5.4 : Electrical Bills Of Quantities
Page No. 16 of 16
References