## SUMMARY
SUMMARY OF BILLS OF QUANTITIES - PRICED
Bill No | DESCRIPTION | AMOUNT
01 | Fire Fighting Equipment - Hydrants, Hose Reels, Extinguishers
02 | Statutory Signage
03 | Fire Sealing
Total Amount for Fire Safety Installations Carried Forward to Main Contract Data (Excl.VAT)

## HYD,FHR,FEs
Bill No. 01 : Fire Fighting Equipment
BUILDINGS: CSIR
(Note : These prices shall be firm and not subject to price adjustment)
1 | PROVISIONAL AND GENERAL ITEMS | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
1.1 | Site Establishment
1.2 | Loading and off loading of material and equipment. | sum | 1
1.3 | Setting out of Works, according to specification | sum | 1
1.4 | Cleaning of site upon completion of contract | sum | 1
1.5 | Detailed Works Programme according to Engineer's specifications | sum | 1
1.6 | Development of workshop drawings, as specified | sum | 1
1.7 | "As-built" drgs in CAD format, as specified | nr | 3
1.8 | Operating and Maintenance Manuals | nr | 3
1.9 | 12-month Maintenance and Guarantee | sum | 1
1.10 | Proving pressure at flow water test | nr | 1
1.11 | Health and Safety Representative | sum | 1
1.12 | P&G’s as per Main Contractor’s conditions | sum | 1
TOTAL FOR THIS PAGE
TOTAL FOR THIS SECTION CARRIED FORWARD TO SUMMARY PAGE
2.1 | FIRE MAINS AND TWIN BOOSTER CONNECTION | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
All equipment as per SABS approved standards:
All costs for connecting, delivery, fittings, connections, bends, junctions and hanging materials to be included.
2.1.1 | booster connection, twin brass 100mm, incl. caps and chains | no | 0
2.1.2 | valve, non return 100mm | no | 0
2.1.3 | valve, butterfly 100mm | no | 0
2.1.4 | Excavate for, locate and cut into existing municipal mains water supply to form connection to new 110mm HDPE fire water supply, incl. backfilling and ramming | lot | 0
2.1.5 | water meter for hydrant/hose reel system | no | 0
2.1.6 | below ground pipe, HDPE 110mm, solvent welded pressure fittings, incl. trenching and backfilling not exceeding 1m deep | m | 0
2.1.7 | below ground pipe, HDPE 110mm, solvent welded pressure fittings, incl. trenching and backfilling not exceeding 2m deep | m | 0
2.1.8 | pipe, med m/s 150mm | m | 0
2.1.9 | pipe, med m/s 100mm | m | 0
2.1.10 | painting 150mm pipe, as per specification | m | 0
2.1.11 | painting 100mm pipe, as per specification | m | 0
TOTAL FOR THIS PAGE
TOTAL CARRIED OVER TO NEXT PAGE
2.2 | FIRE HYDRANTS | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
All equipment as per SABS approved standards.
All costs for connecting, delivery, fittings, connections, bends, junctions and hanging materials to be included.
2.2.1 | hydrant landing valve, brass 100mm, incl cap and chain | no | 0
2.2.2 | pressure gauge, 100mm diameter glycerine filled 1000kPA, incl. stopcock | no | 0
2.2.3 | below ground pipe, HDPE 110mm, solvent welded pressure fittings, incl. trenching and backfilling not exceeding 1m deep | m | 0
2.2.4 | below ground pipe, HDPE 110mm, solvent welded pressure fittings, incl. trenching and backfilling not exceeding 2m deep | m | 0
2.2.5 | pipe, hydrant trunk main, med m/s 150mm | m | 0
2.2.6 | pipe, hydrant trunk main, med m/s 100mm | m | 0
2.2.7 | Unreinforced concrete hydrant pedestal 600mm above natural ground level, cast around vertical pipe with bottom 300mm below ground. 300mmx300mm square at base, tapering to octagonal shaped top 200x200mm overall on 420x420x280mm deep base, incl excavation, formwork and 2 x coats of paint to exposed surfaces | no | 0
2.2.8 | 1000x800mm fire supply valve chamber, comprising brick chamber exceeding 750mm but not exceeding 1000mm deep internally, with cast iron cover and frame size 450x60mm (type CCP) | no | 0
2.2.9 | thrust block, 110mm tee, incl excavation, concrete, formwork, backfilling and ramming | no | 0
2.2.10 | thrust block, 110mm 90deg bend, incl excavation, concrete, formwork, backfilling and ramming | no | 0
2.2.11 | painting 150mm pipe, as per specification | m | 0
2.2.12 | painting 100mm pipe, as per specification | m | 0
TOTAL CARRIED OVER TO NEXT PAGE
2.3 | FIRE HOSE REELS | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
All equipment as per SABS approved standards.
All costs for connecting, delivery, fittings, connections, bends, junctions and hanging materials to be included.
2.3.1 | fire hose reel, c/w 30m hose to EN694 standard, incl. chromium plated stopcock, shut-off nozzle and wall bracket | no | 4
2.3.2 | pressure gauge, 100mm diameter glycerine filled 1000kPA, incl. stopcock | no | 4
2.3.3 | weatherproof fire hose reel cabinet | no | 0
2.3.4 | pipe, med m/s 80mm | m | 0
2.3.5 | pipe, med m/s 65mm | m | 0
2.3.6 | pipe, med m/s 50mm | m | 0
2.3.7 | pipe, med m/s 40mm | m | 0
2.3.8 | pipe, med m/s 32mm | m | 50
2.3.9 | pipe, med m/s 25mm | m | 20
2.3.10 | painting 80mm pipe, as per specification | m | 0
2.3.11 | painting 65mm pipe, as per specification | m | 0
2.3.12 | painting 50mm pipe, as per specification | m | 0
2.3.13 | painting 40mm pipe, as per specification | m | 0
2.3.14 | painting 32mm pipe, as per specification | m | 50
2.3.15 | painting 25mm pipe, as per specification | m | 20
TOTAL FOR THIS PAGE
TOTAL CARRIED OVER TO NEXT PAGE
2.4 | PORTABLE FIRE EXTINGUISHERS | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
All extinguisher as per SABS approved standards.
Extinguishes to be provided each with 25mm thick meranti backing board min. size 150 x 700mm, plugged and screwed to brickwork and all exposed edges bevelled, incl. 1 x coat primer and 2 x coats Signal Red enamel paint. Mounting brackets to be approved in accordance with SABS 810.
2.4.1 | extinguisher, 4,5kg DCP | no | 4
2.4.2 | extinguisher, 9kg DCP | no | 0
2.4.3 | extinguisher, 5kg CO2 | no | 4
2.4.4 | extinguisher, 10kg CO2 | no | 0
2.4.5 | weatherproof extinguisher cabinet for 2-off exting. | no | 0
TOTAL FOR THIS PAGE
TOTAL FOR THIS SECTION CARRIED FORWARD TO SUMMARY PAGE
3 | TESTING AND COMMISSION | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
3.1 | Testing and commission, incl. all labour | Lot | 1
3.2 | ASIB Inspection | Lot | 1
TOTAL FOR THIS PAGE
TOTAL FOR THIS SECTION CARRIED FORWARD TO SUMMARY PAGE
SUMMARY OF BILLS OF QUANTITIES
Section No | DESCRIPTION |  |  | TOTAL
1 | Provisional and General items
2 | Fire Fighting Installation
3 | Testing and Commission
| Contingency: Works as Yet Unforseen and Unknown |  |  | 10000
TOTAL FOR FIRE FIGHTING COMPLETE INSTALLATION (excl.VAT)
TOTAL FOR FIRE FIGHTING COMPLETE INSTALLATION CARRIED FORWARD (excl.VAT)

## Signage
Bill No. 02 : Statutory Signage
BUILDINGS: CSIR
(Note : These prices shall be firm and not subject to price adjustment)
1 | PROVISIONAL AND GENERAL ITEMS | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
1.1 | Loading and off loading of material and equipment. | sum | 1
1.2 | Setting out of Works, according to specification | sum | 1
1.3 | Cleaning of site upon completion of contract | sum | 1
1.4 | Detailed Works Programme according to Engineer's specifications | sum | 1
1.5 | Operating and Maintenance Manuals | nr | 3
1.6 | 12-month Maintenance and Guarantee | sum | 1
1.7 | Health and Safety Representative | sum | 1
1.8 | P&G’s as per Main Contractor’s conditions | sum | 1
TOTAL FOR THIS PAGE
TOTAL FOR THIS SECTION CARRIED FORWARD TO SUMMARY PAGE
2 | STATUTORY SIGNAGE | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
Supply and installation of aluminium framed SABS 1186 approved photoluminescent type signage, incl. fixing, as detailed below:
2.1.1 | running man + down arrow | no | 10
- Code E3
- single sided, 190 x 190mm
- white lettering
- green background
2.1.2 | running man + left arrow | no | 4
- Code E2
- single sided, 190 x 190mm
- white lettering
- green background
2.1.3 | running man + right arrow | no | 2
- Code E1
- single sided
- white lettering
- green background
2.1.4 | hydrant + hose reel + down arrow | no | 0
- Code F1
- single sided, 190 x 190mm
- red lettering
- white background
2.1.5 | hydrant + hose reel + left arrow | no | 0
- Code F2
- single sided, 190 x 190mm
- red lettering
- white background
2.1.6 | hydrant + hose reel + right arrow | no | 0
- Code F3
- single sided, 190 x 190mm
- red lettering
- white background
2.1.7 | hose reel + extinguisher + down arrow | no | 4
- Code F4
- single sided, 190 x 190mm
- red lettering
- white background
TOTAL FOR THIS PAGE
TOTAL CARRIED OVER TO NEXT PAGE
cont. | STATUTORY SIGNAGE | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
2.1.8 | hose reel + extinguisher + left arrow | no | 4
- Code F5
- single sided, 190 x 190mm
- red lettering
- white background
2.1.9 | hose reel + extinguisher + right arrow | no | 4
- Code F6
- single sided, 190 x 190mm
- red lettering
- white background
2.1.10 | hydrant + hose reel + down arrow | no | 0
- Code F7
- single sided, 190 x 190mm
- red lettering
- white background
2.1.11 | hydrant + hose reel + left arrow | no | 0
- Code F8
- single sided, 190 x 190mm
- red lettering
- white background
2.1.12 | hydrant + hose reel + right arrow | no | 0
- Code F9
- single sided, 190 x 190mm
- red lettering
- white background
2.1.13 | extinguisher + down arrow | no | 0
- Code F13
- single sided, 190 x 190mm
- red lettering
- white background
TOTAL FOR THIS PAGE
TOTAL CARRIED OVER TO NEXT PAGE
cont. | STATUTORY SIGNAGE | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
2.1.14 | extinguisher + left arrow | no | 0
Code F16
- single sided, 190 x 190mm
- red lettering
- white background
2.1.15 | extinguisher + right arrow | no | 0
- Code F19
- single sided, 190 x 190mm
- red lettering
- white background
2.1.16 | hose reel + down arrow | no | 0
- Code F14
- single sided, 190 x 190mm
- red lettering
- white background
2.1.17 | hose reel + left arrow | no | 0
- Code F17
- single sided, 190 x 190mm
- red lettering
- white background
2.1.18 | hose reel + right arrow | no | 0
- Code F17
- single sided, 190 x 190mm
- red lettering
- white background
2.1.19 | FIRE EXIT KEEP CLEAR | no | 4
- Code F45
- green lettering
- white background
2.1.20 | Intermally Illuminated EXIT Signage | no | 0
- 60min battery back-up
- green lettering
- white background
- min. 100mm high lettering
- complete with test button
- SABS mark must be indicated
TOTAL FOR THIS PAGE
TOTAL FOR THIS SECTION CARRIED FORWARD TO SUMMARY PAGE
SUMMARY OF BILLS OF QUANTITIES
Section No | DESCRIPTION |  |  | TOTAL
1 | Provisional and General items
2 | Statutory Signage Installation
| Contingency: Works as Yet Unforseen and Unknown |  |  | 2500
TOTAL FOR STATUTORY SIGNAGE INSTALLATION (excl.VAT)
TOTAL FOR STATUTORY SIGNAGE INSTALLATION CARRIED FORWARD (excl.VAT)

## Fire Stopping
Bill No. 03 : Fire Sealing
BUILDINGS: CSIR
(Note : These prices shall be firm and not subject to price adjustment)
1 | PROVISIONAL AND GENERAL ITEMS | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
1.1 | Loading and off loading of material and equipment. | sum | 1
1.2 | Setting out of Works, according to specification | sum | 1
1.3 | Cleaning of site upon completion of contract | sum | 1
1.4 | Detailed Works Programme according to Engineer's specifications | sum | 1
1.5 | 12-month Maintenance and Guarantee | sum | 1
1.6 | Health and Safety Representative | sum | 1
1.7 | P&G’s as per Main Contractor’s conditions | sum | 1
TOTAL FOR THIS PAGE
TOTAL FOR THIS SECTION CARRIED FORWARD TO SUMMARY PAGE
2 | FIRE SEALING | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
The Tenderer's attention is drawn to the Standard Conditions of Sub-Contract applicable to this contract for his responsibilities in regard thereto.
Tenderers shall supply all materials, tools and labour necessary for installation of the gap and fire seals, to provide complete and fully functional installations.
30, 60 or 120-min fire and smoke rated seals to gaps between brick walls and concrete soffits or columns shall be provided with material as per the Engineers approved specification and details.
2.1 | Nullifire M701 fire rated acrylic fire and smoke rated gap seals, or similar approved and certified product, horizontally along top of walls
2.1.1 | 0-25mm Thick 30-min seals | m | 30
2.1.2 | 0-25mm Thick 60-min seals | m | 70
2.1.3 | 0-25mm Thick 120-min seals | m | 0
2.2 | Nullifire M701 acrylic fire rated mastic fire and smoke rated gap seals, or similar approved and certified product, vertically between brick walls and concrete columns
2.2.1 | 0-25mm Thick 30-min seals | m | 0
2.2.2 | 0-25mm Thick 60-min seals | m | 0
2.2.3 | 0-25mm Thick 120-min seals | m | 0
2.3 | KBS' panel seal and 'Flamastic' coating or other equal and approved fire and smoke rated penetration seals through slabs
2.3.1 | 110mm Diameter 60-min uPVC pipe sleeves | no | 5
2.3.2 | 110mm Diameter 120-min uPVC pipe sleeves | no | 0
2.3.3 | 160mm Diameter 60-min uPVC pipe sleeves | no | 0
2.3.4 | 160mm Diameter 120-min uPVC pipe sleeves | no | 0
TOTAL FOR THIS PAGE
TOTAL CARRIED OVER TO NEXT PAGE
cont. | FIRE SEALING | Unit | QTY | Supply Unit Rate | Installation Unit Rate | Amount
2.4 | 60-min Fire wrapping of electrical cabling penetrations through brick walls
2.4.1 | Dia 20 mm cable | m | 2
2.4.2 | Dia 40 mm cable | m | 2
2.4.3 | Dia 80 mm cable | m | 0
2.5 | 120-min Fire wrapping of electrical cabling penetrations through brick walls
2.5.1 | Dia 20 mm cable | m | 0
2.5.2 | Dia 40 mm cable | m | 0
2.5.3 | Dia 80 mm cable | m | 0
2.6 | Panel seals to service shafts
2.6.1 | 30-min seals | sqm | 0
2.6.2 | 60-min seals | sqm | 5
2.6.3 | 120-min seals | sqm | 0
TOTAL FOR THIS PAGE
TOTAL FOR THIS SECTION CARRIED FORWARD TO SUMMARY PAGE
SUMMARY OF BILLS OF QUANTITIES
Section No | DESCRIPTION |  |  | TOTAL
1 | Provisional and General items
2 | Fire Sealing Installation
| Contingency: Works as Yet Unforseen and Unknown |  |  | 5000
TOTAL FOR FIRE SEALING COMPLETE INSTALLATION (excl.VAT)
TOTAL FOR FIRE SEALING COMPLETE INSTALLATION CARRIED FORWARD (excl.VAT)

## 5.8 Sum
Fire Bills of Quantities
Bill No |  |  | Amount
5.8 | Fire Bills of Quantities | R
| Main Contractors percentage for all mark-ups, attendance, etc on specialist domestic contractor | R
0
| Carried Forward To Section 5.10 : Final Summary | R
CSIR Future PHARMA Facility
Section 5.8 : Fire Bills of Quantities
Page No. 18 of 18