## 3_8" BV Nitrogen Line
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-001
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Ball Valves Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  | Prepared | Checked |  | Approved |  | Status
A |  |  |  | MJ |  |  |  |  | Issued for Internal Review
Data Sheet for 3/8" BSP Ball Valves
No | Rev | Section | Description |  |  |  |  | Data
1 |  | GENERAL DATA | VALVE SIZE RANGE Inch (mm) |  |  |  |  | 3/8"
2 |  |  | VALVE BSI Standard |  |  |  |  | PN40
3 |  |  | VALVE TYPE |  |  |  |  | Brass Manual Ball Valve
4 |  |  | VALVE END CONFIGURATION |  |  |  |  | FxF BSP Thread
5 |  |  | VALVE SERVICE |  |  |  |  | Nitrogen
6 |  |  | VALVE TAG NUMBER
7 |  |  | QAUNTITY |  |  |  |  | 3
8 |  |  | VALVE BORE (FULL / REDUCED) |  |  |  |  | Full Bore
9 |  |  | VALVE STANDARD |  |  |  |  | EN 331
10 |  |  | PIGGABLE |  |  |  |  | No
11 |  | DESIGN DATA | DESIGN PRESSURE (kPa) |  | barg | MAXIMUM: |  | 2500 |  |  | MINIMUM: | Full Vacuum
12 |  |  | TEMPERATURE - DESIGN (°C) |  | °C | MAXIMUM: |  | 65 |  | Note 2 | MINIMUM: | 0
13 |  |  | VALVE ACTUATOR |  |  |  |  | N/A
14 |  |  | VALVE OPERATION - MANUAL |  |  |  |  | Handle
15 |  |  | BODY CONSTRUCTION |  |  |  |  | Three Piece
16 |  |  | BALL TYPE |  |  |  |  | Supplier to advise
17 |  |  | VENT CONNECTION |  |  |  |  | No
18 |  |  | DRAIN CONNECTION |  |  |  |  | No
19 |  |  | PRESSURE RELIEF CONNECTION |  |  |  |  | No
20 |  |  | SEALANT INJECTION CONNECTION |  |  |  |  | Manufacturer's Standard
21 |  |  | SUPPORT LEGS / FEET |  |  |  |  | No
22 |  |  | LIFTING EYES |  |  |  |  | No
23 |  |  | LOCKING FACILITY |  |  |  |  | No
24 |  |  | SURFACE TREATMENT |  |  |  |  | Nickel plated
25 |  | MATERIALS | BODY |  |  |  |  | Nickel Plated Brass CW 617N (EN12165)
26 |  |  | COVER / BONNET |  |  |  |  | Brass CW 617N (EN12165)
27 |  |  | GATE |  |  |  |  | N/A
28 |  |  | BALL |  |  |  |  | Chrome Plated Brass
29 |  |  | DISC |  |  |  |  | N/A
30 |  |  | TRIM |  |  |  |  | Supplier to Advise
31 |  |  | SEALS |  |  |  |  | N/A |  |  |  | Note 2
32 |  |  | GASKETS |  |  |  |  | Manufacturer's Standard - Non Asbestos
33 |  |  | STEM |  |  |  |  | Supplier to Advise
34 |  |  | TRUNNION |  |  |  |  | N/A
35 |  |  | SEAT / RINGS |  |  |  |  | PTFE
36 |  |  | STEM SEAL |  |  |  |  | Supplier to Advise
37 |  |  | BOLTING |  |  |  |  | N/A
38 |  | CODES AND STANDARDS | DESIGN |  |  |  |  | EN 331
39 |  |  | DIMENSIONS |  |  |  |  | Supplier to Advise
40 |  |  | THREADED DIMENSIONS |  |  |  |  | EN 10226-1, ISO 228 Parallel
41 |  |  | FLANGE DIMENSIONS |  |  |  |  | N/A
42 |  |  | WELD END DIMENSIONS |  |  |  |  | N/A
43 |  |  | CERTIFICATION |  |  |  |  | Refer to Project Specification
44 |  |  | FIRE TEST - FIRE SAFE DESIGN |  |  |  |  | N/A
45 |  |  | HYDROSTATIC TEST |  |  |  |  | API 6D - No compressive end loads to be applied
46 |  | TESTING REQUIREMENTS | HYDROSTATIC SHELL TEST PRESSURE |  |  |  |  | API 598
47 |  |  | HYDROSTATIC SEAT TEST PRESSURE |  |  |  |  | API 598
48 |  |  | HIGH PRESSURE TEST |  |  |  |  | API 598
49 |  |  | ISO 5208 LEAKAGE RATE FOR SOFT SEAT |  |  |  |  | Rate A
50 |  |  | ISO 5208 LEAKAGE RATE FOR METAL SEAT |  |  |  |  | Rate D
51 |  |  | RADIOGRAPHIC TESTS |  |  |  |  | ASME B16.34 APPENDIX I
52 |  |  | ULTRASONIC TESTS |  |  |  |  | ASME B16.34 APPENDIX IV
53 |  |  | PENETRANT TESTS |  |  |  |  | ASME B16.34 APPENDIX III
54 |  |  | MAGNETIC PARTICLE TESTS |  |  |  |  | ASME B16.34 APPENDIX II
55 |  |  | MATERIAL CERTIFICATION - EN 10204 3.1.B |  |  |  |  | Required

## 1_2" BV Compressed Air Line
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-001
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Ball Valves Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  | Prepared | Checked |  | Approved |  | Status
A |  |  |  | MJ |  |  |  |  | Issued for Internal Review
Data Sheet for 1/2" BSP Ball Valves
No | Rev | Section | Description |  |  |  |  | Data
1 |  | GENERAL DATA | VALVE SIZE RANGE Inch (mm) |  |  |  |  | 1/2"
2 |  |  | VALVE BSI Standard |  |  |  |  | EN 331 PN40
3 |  |  | VALVE TYPE |  |  |  |  | Brass Manual Ball Valve
4 |  |  | VALVE END CONFIGURATION |  |  |  |  | FxF BSP Thread
5 |  |  | VALVE SERVICE |  |  |  |  | Compressed air
6 |  |  | VALVE TAG NUMBER
7 |  |  | QAUNTITY |  |  |  |  | 5
8 |  |  | VALVE BORE (FULL / REDUCED) |  |  |  |  | Full Bore
9 |  |  | VALVE STANDARD |  |  |  |  | EN 331
10 |  |  | PIGGABLE |  |  |  |  | No
11 |  | DESIGN DATA | DESIGN PRESSURE (kPa) |  | barg | MAXIMUM: |  | 2500 |  |  | MINIMUM: | Full Vacuum
12 |  |  | TEMPERATURE - DESIGN (°C) |  | °C | MAXIMUM: |  | 65 |  | Note 2 | MINIMUM: | 0
13 |  |  | VALVE ACTUATOR |  |  |  |  | N/A
14 |  |  | VALVE OPERATION - MANUAL |  |  |  |  | Handle
15 |  |  | BODY CONSTRUCTION |  |  |  |  | Three Piece
16 |  |  | BALL TYPE |  |  |  |  | Supplier to advise
17 |  |  | VENT CONNECTION |  |  |  |  | No
18 |  |  | DRAIN CONNECTION |  |  |  |  | No
19 |  |  | PRESSURE RELIEF CONNECTION |  |  |  |  | No
20 |  |  | SEALANT INJECTION CONNECTION |  |  |  |  | Manufacturer's Standard
21 |  |  | SUPPORT LEGS / FEET |  |  |  |  | No
22 |  |  | LIFTING EYES |  |  |  |  | No
23 |  |  | LOCKING FACILITY |  |  |  |  | No
24 |  |  | SURFACE TREATMENT |  |  |  |  | Nickel plated
25 |  | MATERIALS | BODY |  |  |  |  | Nickel Plated Brass CW 617N (EN12165)
26 |  |  | COVER / BONNET |  |  |  |  | Brass CW 617N (EN12165)
27 |  |  | GATE |  |  |  |  | N/A
28 |  |  | BALL |  |  |  |  | Chrome Plated Brass
29 |  |  | DISC |  |  |  |  | N/A
30 |  |  | TRIM |  |  |  |  | Supplier to Advise
31 |  |  | SEALS |  |  |  |  | N/A |  |  |  | Note 2
32 |  |  | GASKETS |  |  |  |  | Manufacturer's Standard - Non Asbestos
33 |  |  | STEM |  |  |  |  | Supplier to Advise
34 |  |  | TRUNNION |  |  |  |  | N/A
35 |  |  | SEAT / RINGS |  |  |  |  | PTFE
36 |  |  | STEM SEAL |  |  |  |  | Supplier to Advise
37 |  |  | BOLTING |  |  |  |  | N/A
38 |  | CODES AND STANDARDS | DESIGN |  |  |  |  | EN 331
39 |  |  | DIMENSIONS |  |  |  |  | Supplier to Advise
40 |  |  | THREADED DIMENSIONS |  |  |  |  | EN 10226-1, ISO 228 Parallel
41 |  |  | FLANGE DIMENSIONS |  |  |  |  | N/A
42 |  |  | WELD END DIMENSIONS |  |  |  |  | N/A
43 |  |  | CERTIFICATION |  |  |  |  | Refer to Project Specification
44 |  |  | FIRE TEST - FIRE SAFE DESIGN |  |  |  |  | N/A
45 |  |  | HYDROSTATIC TEST |  |  |  |  | API 6D - No compressive end loads to be applied
46 |  | TESTING REQUIREMENTS | HYDROSTATIC SHELL TEST PRESSURE |  |  |  |  | API 598
47 |  |  | HYDROSTATIC SEAT TEST PRESSURE |  |  |  |  | API 598
48 |  |  | HIGH PRESSURE TEST |  |  |  |  | API 598
49 |  |  | ISO 5208 LEAKAGE RATE FOR SOFT SEAT |  |  |  |  | Rate A
50 |  |  | ISO 5208 LEAKAGE RATE FOR METAL SEAT |  |  |  |  | Rate D
51 |  |  | RADIOGRAPHIC TESTS |  |  |  |  | ASME B16.34 APPENDIX I
52 |  |  | ULTRASONIC TESTS |  |  |  |  | ASME B16.34 APPENDIX IV
53 |  |  | PENETRANT TESTS |  |  |  |  | ASME B16.34 APPENDIX III
54 |  |  | MAGNETIC PARTICLE TESTS |  |  |  |  | ASME B16.34 APPENDIX II
55 |  |  | MATERIAL CERTIFICATION - EN 10204 3.1.B |  |  |  |  | Required

## 15mm BV Municipal Water Line
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-001
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Ball Valves Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  | Prepared | Checked |  | Approved |  | Status
A |  |  |  | MJ |  |  |  |  | Issued for Internal Review
Data Sheet for 15mm BSP Ball Valves
No | Rev | Section | Description |  |  |  |  | Data
1 |  | GENERAL DATA | VALVE SIZE RANGE Inch (mm) |  |  |  |  | 15mm
2 |  |  | VALVE BSI Standard |  |  |  |  | EN 331 PN40
3 |  |  | VALVE TYPE |  |  |  |  | Brass Manual Ball Valve
4 |  |  | VALVE END CONFIGURATION |  |  |  |  | FxF BSP Thread
5 |  |  | VALVE SERVICE |  |  |  |  | Municipal (Potable) Water
6 |  |  | VALVE TAG NUMBER
7 |  |  | QAUNTITY |  |  |  |  | 12
8 |  |  | VALVE BORE (FULL / REDUCED) |  |  |  |  | Full Bore
9 |  |  | VALVE STANDARD |  |  |  |  | EN 331
10 |  |  | PIGGABLE |  |  |  |  | No
11 |  | DESIGN DATA | DESIGN PRESSURE (kPa) |  | barg | MAXIMUM: |  | 1500 |  |  | MINIMUM: | Full Vacuum
12 |  |  | TEMPERATURE - DESIGN (°C) |  | °C | MAXIMUM: |  | 40 |  | Note 2 | MINIMUM: | 0
13 |  |  | VALVE ACTUATOR |  |  |  |  | N/A
14 |  |  | VALVE OPERATION - MANUAL |  |  |  |  | Handle
15 |  |  | BODY CONSTRUCTION |  |  |  |  | Three Piece
16 |  |  | BALL TYPE |  |  |  |  | Supplier to advise
17 |  |  | VENT CONNECTION |  |  |  |  | No
18 |  |  | DRAIN CONNECTION |  |  |  |  | No
19 |  |  | PRESSURE RELIEF CONNECTION |  |  |  |  | No
20 |  |  | SEALANT INJECTION CONNECTION |  |  |  |  | Manufacturer's Standard
21 |  |  | SUPPORT LEGS / FEET |  |  |  |  | No
22 |  |  | LIFTING EYES |  |  |  |  | No
23 |  |  | LOCKING FACILITY |  |  |  |  | No
24 |  |  | SURFACE TREATMENT |  |  |  |  | Nickel plated
25 |  | MATERIALS | BODY |  |  |  |  | Nickel Plated Brass CW 617N (EN12165)
26 |  |  | COVER / BONNET |  |  |  |  | Brass CW 617N (EN12165)
27 |  |  | GATE |  |  |  |  | N/A
28 |  |  | BALL |  |  |  |  | Chrome Plated Brass
29 |  |  | DISC |  |  |  |  | N/A
30 |  |  | TRIM |  |  |  |  | Supplier to Advise
31 |  |  | SEALS |  |  |  |  | N/A |  |  |  | Note 2
32 |  |  | GASKETS |  |  |  |  | Manufacturer's Standard - Non Asbestos
33 |  |  | STEM |  |  |  |  | Supplier to Advise
34 |  |  | TRUNNION |  |  |  |  | N/A
35 |  |  | SEAT / RINGS |  |  |  |  | PTFE
36 |  |  | STEM SEAL |  |  |  |  | Supplier to Advise
37 |  |  | BOLTING |  |  |  |  | N/A
38 |  | CODES AND STANDARDS | DESIGN |  |  |  |  | EN 331
39 |  |  | DIMENSIONS |  |  |  |  | Supplier to Advise
40 |  |  | THREADED DIMENSIONS |  |  |  |  | EN 10226-1, ISO 228 Parallel
41 |  |  | FLANGE DIMENSIONS |  |  |  |  | N/A
42 |  |  | WELD END DIMENSIONS |  |  |  |  | N/A
43 |  |  | CERTIFICATION |  |  |  |  | Refer to Project Specification
44 |  |  | FIRE TEST - FIRE SAFE DESIGN |  |  |  |  | N/A
45 |  |  | HYDROSTATIC TEST |  |  |  |  | API 6D - No compressive end loads to be applied
46 |  | TESTING REQUIREMENTS | HYDROSTATIC SHELL TEST PRESSURE |  |  |  |  | API 598
47 |  |  | HYDROSTATIC SEAT TEST PRESSURE |  |  |  |  | API 598
48 |  |  | HIGH PRESSURE TEST |  |  |  |  | API 598
49 |  |  | ISO 5208 LEAKAGE RATE FOR SOFT SEAT |  |  |  |  | Rate A
50 |  |  | ISO 5208 LEAKAGE RATE FOR METAL SEAT |  |  |  |  | Rate D
51 |  |  | RADIOGRAPHIC TESTS |  |  |  |  | ASME B16.34 APPENDIX I
52 |  |  | ULTRASONIC TESTS |  |  |  |  | ASME B16.34 APPENDIX IV
53 |  |  | PENETRANT TESTS |  |  |  |  | ASME B16.34 APPENDIX III
54 |  |  | MAGNETIC PARTICLE TESTS |  |  |  |  | ASME B16.34 APPENDIX II
55 |  |  | MATERIAL CERTIFICATION - EN 10204 3.1.B |  |  |  |  | Required

## 15mm Hot Geyser Water Line
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-001
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Ball Valves Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  | Prepared | Checked |  | Approved |  | Status
A |  |  |  | MJ |  |  |  |  | Issued for Internal Review
Data Sheet for 15mm BSP Ball Valves
No | Rev | Section | Description |  |  |  |  | Data
1 |  | GENERAL DATA | VALVE SIZE RANGE Inch (mm) |  |  |  |  | 15mm
2 |  |  | VALVE BSI Standard |  |  |  |  | EN 331 PN40
3 |  |  | VALVE TYPE |  |  |  |  | Brass Manual Ball Valve
4 |  |  | VALVE END CONFIGURATION |  |  |  |  | FxF BSP Thread
5 |  |  | VALVE SERVICE |  |  |  |  | Municipal (Potable) Water
6 |  |  | VALVE TAG NUMBER
7 |  |  | QAUNTITY |  |  |  |  | 4
8 |  |  | VALVE BORE (FULL / REDUCED) |  |  |  |  | Full Bore
9 |  |  | VALVE STANDARD |  |  |  |  | EN 331
10 |  |  | PIGGABLE |  |  |  |  | No
11 |  | DESIGN DATA | DESIGN PRESSURE (kPa) |  | barg | MAXIMUM: |  | 1500 |  |  | MINIMUM: | Full Vacuum
12 |  |  | TEMPERATURE - DESIGN (°C) |  | °C | MAXIMUM: |  | 65 |  | Note 2 | MINIMUM: | 0
13 |  |  | VALVE ACTUATOR |  |  |  |  | N/A
14 |  |  | VALVE OPERATION - MANUAL |  |  |  |  | Handle
15 |  |  | BODY CONSTRUCTION |  |  |  |  | Three Piece
16 |  |  | BALL TYPE |  |  |  |  | Supplier to advise
17 |  |  | VENT CONNECTION |  |  |  |  | No
18 |  |  | DRAIN CONNECTION |  |  |  |  | No
19 |  |  | PRESSURE RELIEF CONNECTION |  |  |  |  | No
20 |  |  | SEALANT INJECTION CONNECTION |  |  |  |  | Manufacturer's Standard
21 |  |  | SUPPORT LEGS / FEET |  |  |  |  | No
22 |  |  | LIFTING EYES |  |  |  |  | No
23 |  |  | LOCKING FACILITY |  |  |  |  | No
24 |  |  | SURFACE TREATMENT |  |  |  |  | Nickel plated
25 |  | MATERIALS | BODY |  |  |  |  | Nickel Plated Brass CW 617N (EN12165)
26 |  |  | COVER / BONNET |  |  |  |  | Brass CW 617N (EN12165)
27 |  |  | GATE |  |  |  |  | N/A
28 |  |  | BALL |  |  |  |  | Chrome Plated Brass
29 |  |  | DISC |  |  |  |  | N/A
30 |  |  | TRIM |  |  |  |  | Supplier to Advise
31 |  |  | SEALS |  |  |  |  | N/A |  |  |  | Note 2
32 |  |  | GASKETS |  |  |  |  | Manufacturer's Standard - Non Asbestos
33 |  |  | STEM |  |  |  |  | Supplier to Advise
34 |  |  | TRUNNION |  |  |  |  | N/A
35 |  |  | SEAT / RINGS |  |  |  |  | PTFE
36 |  |  | STEM SEAL |  |  |  |  | Supplier to Advise
37 |  |  | BOLTING |  |  |  |  | N/A
38 |  | CODES AND STANDARDS | DESIGN |  |  |  |  | EN 331
39 |  |  | DIMENSIONS |  |  |  |  | Supplier to Advise
40 |  |  | THREADED DIMENSIONS |  |  |  |  | EN 10226-1, ISO 228 Parallel
41 |  |  | FLANGE DIMENSIONS |  |  |  |  | N/A
42 |  |  | WELD END DIMENSIONS |  |  |  |  | N/A
43 |  |  | CERTIFICATION |  |  |  |  | Refer to Project Specification
44 |  |  | FIRE TEST - FIRE SAFE DESIGN |  |  |  |  | N/A
45 |  |  | HYDROSTATIC TEST |  |  |  |  | API 6D - No compressive end loads to be applied
46 |  | TESTING REQUIREMENTS | HYDROSTATIC SHELL TEST PRESSURE |  |  |  |  | API 598
47 |  |  | HYDROSTATIC SEAT TEST PRESSURE |  |  |  |  | API 598
48 |  |  | HIGH PRESSURE TEST |  |  |  |  | API 598
49 |  |  | ISO 5208 LEAKAGE RATE FOR SOFT SEAT |  |  |  |  | Rate A
50 |  |  | ISO 5208 LEAKAGE RATE FOR METAL SEAT |  |  |  |  | Rate D
51 |  |  | RADIOGRAPHIC TESTS |  |  |  |  | ASME B16.34 APPENDIX I
52 |  |  | ULTRASONIC TESTS |  |  |  |  | ASME B16.34 APPENDIX IV
53 |  |  | PENETRANT TESTS |  |  |  |  | ASME B16.34 APPENDIX III
54 |  |  | MAGNETIC PARTICLE TESTS |  |  |  |  | ASME B16.34 APPENDIX II
55 |  |  | MATERIAL CERTIFICATION - EN 10204 3.1.B |  |  |  |  | Required

## 22mm Hot Geyser Water Line
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-002
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Ball Valves Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  | Prepared | Checked |  | Approved |  | Status
A |  |  |  | MJ |  |  |  |  | Issued for Internal Review
Data Sheet for 22mm BSP Ball Valves
No | Rev | Section | Description |  |  |  |  | Data
1 |  | GENERAL DATA | VALVE SIZE RANGE Inch (mm) |  |  |  |  | 22mm
2 |  |  | VALVE BSI Standard |  |  |  |  | EN 331 PN40
3 |  |  | VALVE TYPE |  |  |  |  | Brass Manual Ball Valve
4 |  |  | VALVE END CONFIGURATION |  |  |  |  | FxF BSP Thread
5 |  |  | VALVE SERVICE |  |  |  |  | Municipal (Potable) Water
6 |  |  | VALVE TAG NUMBER
7 |  |  | QAUNTITY |  |  |  |  | 1
8 |  |  | VALVE BORE (FULL / REDUCED) |  |  |  |  | Full Bore
9 |  |  | VALVE STANDARD |  |  |  |  | EN 331
10 |  |  | PIGGABLE |  |  |  |  | No
11 |  | DESIGN DATA | DESIGN PRESSURE (kPa) |  | barg | MAXIMUM: |  | 1500 |  |  | MINIMUM: | Full Vacuum
12 |  |  | TEMPERATURE - DESIGN (°C) |  | °C | MAXIMUM: |  | 65 |  | Note 2 | MINIMUM: | 0
13 |  |  | VALVE ACTUATOR |  |  |  |  | N/A
14 |  |  | VALVE OPERATION - MANUAL |  |  |  |  | Handle
15 |  |  | BODY CONSTRUCTION |  |  |  |  | Three Piece
16 |  |  | BALL TYPE |  |  |  |  | Supplier to advise
17 |  |  | VENT CONNECTION |  |  |  |  | No
18 |  |  | DRAIN CONNECTION |  |  |  |  | No
19 |  |  | PRESSURE RELIEF CONNECTION |  |  |  |  | No
20 |  |  | SEALANT INJECTION CONNECTION |  |  |  |  | Manufacturer's Standard
21 |  |  | SUPPORT LEGS / FEET |  |  |  |  | No
22 |  |  | LIFTING EYES |  |  |  |  | No
23 |  |  | LOCKING FACILITY |  |  |  |  | No
24 |  |  | SURFACE TREATMENT |  |  |  |  | Nickel plated
25 |  | MATERIALS | BODY |  |  |  |  | Nickel Plated Brass CW 617N (EN12165)
26 |  |  | COVER / BONNET |  |  |  |  | Brass CW 617N (EN12165)
27 |  |  | GATE |  |  |  |  | N/A
28 |  |  | BALL |  |  |  |  | Chrome Plated Brass
29 |  |  | DISC |  |  |  |  | N/A
30 |  |  | TRIM |  |  |  |  | Supplier to Advise
31 |  |  | SEALS |  |  |  |  | N/A |  |  |  | Note 2
32 |  |  | GASKETS |  |  |  |  | Manufacturer's Standard - Non Asbestos
33 |  |  | STEM |  |  |  |  | Supplier to Advise
34 |  |  | TRUNNION |  |  |  |  | N/A
35 |  |  | SEAT / RINGS |  |  |  |  | PTFE
36 |  |  | STEM SEAL |  |  |  |  | Supplier to Advise
37 |  |  | BOLTING |  |  |  |  | N/A
38 |  | CODES AND STANDARDS | DESIGN |  |  |  |  | EN 331
39 |  |  | DIMENSIONS |  |  |  |  | Supplier to Advise
40 |  |  | THREADED DIMENSIONS |  |  |  |  | EN 10226-1, ISO 228 Parallel
41 |  |  | FLANGE DIMENSIONS |  |  |  |  | N/A
42 |  |  | WELD END DIMENSIONS |  |  |  |  | N/A
43 |  |  | CERTIFICATION |  |  |  |  | Refer to Project Specification
44 |  |  | FIRE TEST - FIRE SAFE DESIGN |  |  |  |  | N/A
45 |  |  | HYDROSTATIC TEST |  |  |  |  | API 6D - No compressive end loads to be applied
46 |  | TESTING REQUIREMENTS | HYDROSTATIC SHELL TEST PRESSURE |  |  |  |  | API 598
47 |  |  | HYDROSTATIC SEAT TEST PRESSURE |  |  |  |  | API 598
48 |  |  | HIGH PRESSURE TEST |  |  |  |  | API 598
49 |  |  | ISO 5208 LEAKAGE RATE FOR SOFT SEAT |  |  |  |  | Rate A
50 |  |  | ISO 5208 LEAKAGE RATE FOR METAL SEAT |  |  |  |  | Rate D
51 |  |  | RADIOGRAPHIC TESTS |  |  |  |  | ASME B16.34 APPENDIX I
52 |  |  | ULTRASONIC TESTS |  |  |  |  | ASME B16.34 APPENDIX IV
53 |  |  | PENETRANT TESTS |  |  |  |  | ASME B16.34 APPENDIX III
54 |  |  | MAGNETIC PARTICLE TESTS |  |  |  |  | ASME B16.34 APPENDIX II
55 |  |  | MATERIAL CERTIFICATION - EN 10204 3.1.B |  |  |  |  | Required

## 0.5" SW BV
Project |  |  | Import PRMS and Pipeline
Document No: |  |  | 19063-HIT-ME-DAS-005
Location: |  |  | Tema, Ghana
Item: |  |  | Line valve Data Sheet
Page: |  |  | 7 of 22
Revision Tracking
Rev No. |  | Date |  | Prepared | Checked |  | Approved |  | Status
A |  | 13/09/2021 |  | MJ |  |  |  |  | Issued for Internal Review
Data Sheet for 1/2" Socket Weld Ball Valves
No | Rev | Section | Description |  |  |  |  | Data
1 |  | GENERAL DATA | VALVE SIZE RANGE |  | Inch (mm) |  |  | 1/2"
2 |  |  | VALVE ASME CLASS |  |  |  |  | 300- SCH40
3 |  |  | VALVE TYPE |  |  |  |  | Ball Valve, Trunnion Mounted
4 |  |  | VALVE END CONFIGURATION |  |  |  |  | Socket Weld
5 |  |  | VALVE SERVICE |  |  |  |  | Natural Gas
6 |  |  | VALVE TAG NUMBER
7 |  |  | QUANTITY |  |  |  |  | 8
8 |  |  | VALVE BORE (FULL / REDUCED) |  |  |  |  | Full Bore
9 |  |  | VALVE STANDARD |  |  |  |  | ASME B16.34 / API 608
10 |  |  | PIGGABLE |  |  |  |  | No
11 |  | DESIGN DATA | DESIGN PRESSURE (kPa) |  | barg | MAXIMUM: |  | 2500 |  |  | MINIMUM: | Full Vacuum
12 |  |  | TEMPERATURE - DESIGN (°C) |  | °C | MAXIMUM: |  | 220 |  | Note 2 | MINIMUM: | 0
13 |  |  | VALVE ACTUATOR |  |  |  |  | N/A
14 |  |  | VALVE OPERATION - MANUAL |  |  |  |  | Hand Lever
15 |  |  | VENT CONNECTION |  |  |  |  | N/A
16 |  |  | DRAIN CONNECTION |  |  |  |  | N/A
17 |  |  | PRESSURE RELIEF CONNECTION |  |  |  |  | N/A
18 |  |  | SEALANT INJECTION CONNECTION |  |  |  |  | Manufacturer's Standard
19 |  |  | SUPPORT LEGS / FEET |  |  |  |  | N/A
20 |  |  | LIFTING EYES |  |  |  |  | N/A
21 |  |  | LOCKING FACILITY |  |  |  |  | Yes |  |  |  |  | Note 13
22 |  |  | SURFACE TREATMENT |  |  |  |  | 50 microns Zinc Phosphate Primer + Paint Specification for Above Ground. |  |  |  |  | Note 4
23 |  | MATERIALS | BODY |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 105
24 |  |  | COVER / BONNET |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 105
25 |  |  | GATE |  |  |  |  | N/A
26 |  |  | BALL |  |  |  |  | Supplier to Advise
27 |  |  | DISC |  |  |  |  | N/A
28 |  |  | TRIM |  |  |  |  | Supplier to Advise
29 |  |  | SEALS |  |  |  |  | Viton / Graphite |  |  |  | Note 2 | Note 2
30 |  |  | GASKETS |  |  |  |  | Manufacturer's Standard - Non Asbestos
31 |  |  | STEM |  |  |  |  | SS304 (VTA) |  |  |  |  | Note 3
32 |  |  | TRUNNION |  |  |  |  | N/A
33 |  |  | SEAT / RINGS |  |  |  |  | Supplier to Advise
34 |  |  | STEM SEAL |  |  |  |  | Viton / 316 / Graphite |  |  |  |  | Note 2
35 |  |  | BOLTING |  |  |  |  | ASTM A193 B7, ASTM A194 2H |  |  |  |  | Note 9
36 |  | CODES AND STANDARDS | DESIGN |  |  |  |  | API 6D
37 |  |  | DIMENSIONS |  |  |  |  | ASME B16.10
38 |  |  | THREADED DIMENSIONS |  |  |  |  | N/A
39 |  |  | FLANGE DIMENSIONS |  |  |  |  | N/A
40 |  |  | WELD END DIMENSIONS |  |  |  |  | ASME B16.11
41 |  |  | CERTIFICATION |  |  |  |  | Refer to Project Specification
42 |  |  | FIRE TEST - FIRE SAFE DESIGN |  |  |  |  | API 6FA / API 607 / BS 6755 Part 2
43 |  |  | HYDROSTATIC TEST |  |  |  |  | API 6D - No compressive end loads to be applied |  |  |  |  | Note 1
44 |  | TESTING REQUIREMENTS | HYDROSTATIC SHELL TEST PRESSURE |  |  |  |  | API 598
45 |  |  | HYDROSTATIC SEAT TEST PRESSURE |  |  |  |  | API 598
46 |  |  | HIGH PRESSURE TEST |  |  |  |  | API 598
47 |  |  | ISO 5208 LEAKAGE RATE FOR SOFT SEAT |  |  |  |  | Rate A
48 |  |  | ISO 5208 LEAKAGE RATE FOR METAL SEAT |  |  |  |  | Rate D
49 |  |  | RADIOGRAPHIC TESTS |  |  |  |  | ASME B16.34 APPENDIX I
50 |  |  | ULTRASONIC TESTS |  |  |  |  | ASME B16.34 APPENDIX IV
51 |  |  | PENETRANT TESTS |  |  |  |  | ASME B16.34 APPENDIX III
52 |  |  | MAGNETIC PARTICLE TESTS |  |  |  |  | ASME B16.34 APPENDIX II
53 |  |  | MATERIAL CERTIFICATION - EN 10204 3.1.B |  |  |  |  | Required

## Steam Line 1.5" SW PV
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-002
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Ball Valves Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  | Prepared | Checked |  | Approved |  | Status
A |  | 2021-09-11 |  | MJ | JvdW |  | CP |  | Issued for Internal Review
Data Sheet for 1 1/2" Socket Weld Plug Valves
No | Rev | Section | Description |  |  |  |  | Data
1 |  | GENERAL DATA | VALVE SIZE RANGE |  | Inch (mm) |  |  | 1,5" (48.3mm)
2 |  |  | VALVE ASME CLASS |  |  |  |  | 300 - SCH 40
3 |  |  | VALVE TYPE |  |  |  |  | Plug Valve
4 |  |  | VALVE END CONFIGURATION |  |  |  |  | Socket Weld
5 |  |  | VALVE SERVICE |  |  |  |  | Steam
6 |  |  | VALVE TAG NUMBER
7 |  |  | QUANTITY |  |  |  |  | 1
8 |  |  | VALVE BORE (FULL / REDUCED) |  |  |  |  | Full Bore
9 |  |  | VALVE STANDARD |  |  |  |  | ASME B16.34 / API 6D
10 |  |  | PIGGABLE |  |  |  |  | No
11 |  | DESIGN DATA | DESIGN PRESSURE (kPa) |  | barg | MAXIMUM: |  | 2500 |  |  | MINIMUM: | Full Vacuum
12 |  |  | TEMPERATURE - DESIGN (°C) |  | °C | MAXIMUM: |  | 220 |  | Note 2 | MINIMUM: | 0
13 |  |  | VALVE ACTUATOR |  |  |  |  | N/A
14 |  |  | VALVE OPERATION - MANUAL |  |  |  |  | Hand Lever
15 |  |  | VENT CONNECTION |  |  |  |  | N/A
16 |  |  | DRAIN CONNECTION |  |  |  |  | N/A
17 |  |  | PRESSURE RELIEF CONNECTION |  |  |  |  | N/A
18 |  |  | SEALANT INJECTION CONNECTION |  |  |  |  | Manufacturer's Standard
19 |  |  | SUPPORT LEGS / FEET |  |  |  |  | N/A
20 |  |  | LIFTING EYES |  |  |  |  | N/A
21 |  |  | LOCKING FACILITY |  |  |  |  | Yes
22 |  |  | SURFACE TREATMENT |  |  |  |  | 50 microns Zinc Phosphate Primer + Paint Specification for Above Ground.
23 |  | MATERIALS | BODY |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 105
24 |  |  | COVER / BONNET |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 105
25 |  |  | GATE |  |  |  |  | N/A
26 |  |  | BALL |  |  |  |  | Supplier to Advise
27 |  |  | DISC |  |  |  |  | N/A
28 |  |  | TRIM |  |  |  |  | Supplier to Advise
29 |  |  | SEALS |  |  |  |  | Supplier to advise |  |  |  | Note 2
30 |  |  | GASKETS |  |  |  |  | Manufacturer's Standard - Non Asbestos
31 |  |  | STEM |  |  |  |  | Supplier to advise
32 |  |  | TRUNNION |  |  |  |  | N/A
33 |  |  | SEAT / RINGS |  |  |  |  | VTC
34 |  |  | STEM SEAL |  |  |  |  | Supplier to Advise
35 |  |  | BOLTING |  |  |  |  | ASTM A193 B7, ASTM A194 2H
36 |  | CODES AND STANDARDS | DESIGN |  |  |  |  | API 6D
37 |  |  | DIMENSIONS |  |  |  |  | ASME B16.10
38 |  |  | THREADED DIMENSIONS |  |  |  |  | N/A
39 |  |  | FLANGE DIMENSIONS |  |  |  |  | N/A
40 |  |  | WELD END DIMENSIONS |  |  |  |  | ASME B16.11
41 |  |  | CERTIFICATION |  |  |  |  | Refer to Project Specification
42 |  |  | FIRE TEST - FIRE SAFE DESIGN |  |  |  |  | API 6FA / API 607 / BS 6755 Part 2
43 |  |  | HYDROSTATIC TEST |  |  |  |  | API 6D - No compressive end loads to be applied
44 |  | TESTING REQUIREMENTS | HYDROSTATIC SHELL TEST PRESSURE |  |  |  |  | API 598
45 |  |  | HYDROSTATIC SEAT TEST PRESSURE |  |  |  |  | API 598
46 |  |  | HIGH PRESSURE TEST |  |  |  |  | API 598
47 |  |  | ISO 5208 LEAKAGE RATE FOR SOFT SEAT |  |  |  |  | Rate A
48 |  |  | ISO 5208 LEAKAGE RATE FOR METAL SEAT |  |  |  |  | Rate D
49 |  |  | RADIOGRAPHIC TESTS |  |  |  |  | ASME B16.34 APPENDIX I
50 |  |  | ULTRASONIC TESTS |  |  |  |  | ASME B16.34 APPENDIX IV
51 |  |  | PENETRANT TESTS |  |  |  |  | ASME B16.34 APPENDIX III
52 |  |  | MAGNETIC PARTICLE TESTS |  |  |  |  | ASME B16.34 APPENDIX II
53 |  |  | MATERIAL CERTIFICATION - EN 10204 3.1.B |  |  |  |  | Required

## Steam Line 3_8" SW NV
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-002
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Ball Valves Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  | Prepared | Checked |  | Approved |  | Status
A |  | 2021-09-11 |  | MJ |  |  |  |  | Issued for Internal Review
Data Sheet for 3/8" Socket Weld Needle Valve
No | Rev | Section | Description |  |  |  |  | Data
1 |  | GENERAL DATA | VALVE SIZE RANGE |  | Inch (mm) |  |  | 3/8"
2 |  |  | VALVE ASME CLASS |  |  |  |  | 300 - SCH40
3 |  |  | VALVE TYPE |  |  |  |  | Needle valve
4 |  |  | VALVE END CONFIGURATION |  |  |  |  | Socket Weld - SCH 40
5 |  |  | VALVE SERVICE |  |  |  |  | Steam
6 |  |  | VALVE TAG NUMBER
7 |  |  | QUANTITY |  |  |  |  | 1
8 |  |  | VALVE BORE (FULL / REDUCED) |  |  |  |  | Full
9 |  |  | VALVE STANDARD |  |  |  |  | ASME B16.34 / API 594
10 |  |  | PIGGABLE |  |  |  |  | No
11 |  | DESIGN DATA | DESIGN PRESSURE (kPa) |  | barg | MAXIMUM: |  | 2500 |  |  | MINIMUM: | Full Vacuum
12 |  |  | TEMPERATURE - DESIGN (°C) |  | °C | MAXIMUM: |  | 220 |  | Note 2 | MINIMUM: | 0
13 |  |  | VALVE ACTUATOR |  |  |  |  | N/A
14 |  |  | VALVE OPERATION - MANUAL |  |  |  |  | N/A
15 |  |  | VENT CONNECTION |  |  |  |  | N/A
16 |  |  | DRAIN CONNECTION |  |  |  |  | N/A
17 |  |  | PRESSURE RELIEF CONNECTION |  |  |  |  | N/A
18 |  |  | SEALANT INJECTION CONNECTION |  |  |  |  | Manufacturer's Standard
19 |  |  | SUPPORT LEGS / FEET |  |  |  |  | Yes
20 |  |  | LIFTING EYES |  |  |  |  | Yes
21 |  |  | LOCKING FACILITY |  |  |  |  | No
22 |  |  | SURFACE TREATMENT |  |  |  |  | 50 microns Zinc Phosphate Primer + Paint Specification for Above Ground.
23 |  | MATERIALS | BODY |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 216 WCB / A 105
24 |  |  | COVER / BONNET |  |  |  |  | Carbon Steel (API 6D Approved) ASTM A 216 WCB / A 105
25 |  |  | GATE |  |  |  |  | N/A
26 |  |  | BALL |  |  |  |  | N/A
27 |  |  | DISC |  |  |  |  | VTC
28 |  |  | TRIM |  |  |  |  | VTC
29 |  |  | SEALS |  |  |  |  | Viton / Graphite |  |  |  | Note 2
30 |  |  | GASKETS |  |  |  |  | Manufacturer's Standard - Non Asbestos
31 |  |  | STEM |  |  |  |  | N/A
32 |  |  | TRUNNION |  |  |  |  | N/A
33 |  |  | SEAT / RINGS |  |  |  |  | VTC
34 |  |  | STEM SEAL |  |  |  |  | N/A
35 |  |  | BOLTING |  |  |  |  | ASTM A193 B7, ASTM A194 2H
36 |  | CODES AND STANDARDS | DESIGN |  |  |  |  | API 6D
37 |  |  | DIMENSIONS |  |  |  |  | ASME B16.10
38 |  |  | THREADED DIMENSIONS |  |  |  |  | N/A
39 |  |  | FLANGE DIMENSIONS |  |  |  |  | ASME B16.5
40 |  |  | WELD END DIMENSIONS |  |  |  |  | N/A
41 |  |  | CERTIFICATION |  |  |  |  | Refer to Project Specification
42 |  |  | FIRE TEST - FIRE SAFE DESIGN |  |  |  |  | API 6FA / API 607 / BS 6755 Part 2 / API 6FD
43 |  |  | HYDROSTATIC TEST |  |  |  |  | API 6D - No compressive end loads to be applied |  |  |  |  | Note 1
44 |  | TESTING REQUIREMENTS | HYDROSTATIC SHELL TEST PRESSURE |  |  |  |  | API 598
45 |  |  | HYDROSTATIC SEAT TEST PRESSURE |  |  |  |  | API 598
46 |  |  | HIGH PRESSURE TEST |  |  |  |  | API 598
47 |  |  | ISO 5208 LEAKAGE RATE FOR SOFT SEAT |  |  |  |  | Rate A
48 |  |  | ISO 5208 LEAKAGE RATE FOR METAL SEAT |  |  |  |  | Rate D
49 |  |  | RADIOGRAPHIC TESTS |  |  |  |  | ASME B16.34 APPENDIX I
50 |  |  | ULTRASONIC TESTS |  |  |  |  | ASME B16.34 APPENDIX IV
51 |  |  | PENETRANT TESTS |  |  |  |  | ASME B16.34 APPENDIX III
52 |  |  | MAGNETIC PARTICLE TESTS |  |  |  |  | ASME B16.34 APPENDIX II
53 |  |  | MATERIAL CERTIFICATION - EN 10204 3.1.B |  |  |  |  | Required