## Nitrogen Line_
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-001
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Nitrogen Line Connections Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  |  | Prepared |  |  | Checked |  | Approved |  | Status
A |  |  |  |  | MJ | [6 empty] | Issued for Internal Review
Data Sheet for Nitrogen Line Connections and Tubing
No | Rev | Section | Data | [5 empty] | Description
1 |  | DESIGN DATA | TRANSPORTED FLUID | [7 empty] | Nitrogen
2 |  |  | LOCATION | [7 empty] | Above Ground
3 |  |  | DESIGN LIFE | [7 empty] | 25 years
4 |  |  | PIPELINE DESIGN PRESSURE |  |  |  | Barg |  |  |  | 25
5 |  |  | PIPELINE TEMPERATURE - DESIGN |  |  |  |  | °C | MAXIMUM |  | 65 |  | Note 2 | MINIMUM: | 0
6 |  |  | SERVICE TYPE (Sour/ Non-sour) |  |  |  |  | barg |  |  | Non-sour
7 |  |  | TUBING MATERIAL | [7 empty] | Medical Grade Copper SANS 1453:2011 (Imperial)
8 |  |  | TUBING FITTING MATERIAL | [7 empty] | VTC
9 |  |  | TUBING FITTING THREAD | [7 empty] | NPT and BSP
10 |  |  | TUBING FITTING TYPE | [7 empty] | Compression fitting (Ferrule type) (VTC)
11 |  |  | Notes
12 |  |  | 1 | VTC - VENDOR TO CONFIRM
13 |  |  | 2 | Supplier to confirm tubing for specified Pressures and Temperatures
14
15
16 | [10 empty] | VENDOR TO CONFIRM
17 |  | Material and Quantities | Description |  |  | End Connection |  |  | Size |  | Quantity |  |  |  |  | Connection Material | Notes
18 |  |  | Medical Cu Tube |  |  | - |  |  | 3/8" |  | 30.48mtrs 2 rols of 15,24mtrs (Note 2)
19 |  |  | PID 10 - Main Utilities Connections
20 |  |  | Male connector |  |  | 3/8" tube X 1/2" npt male |  |  | 3/8" |  | 2 |  |  |  |  | Brass
21 |  |  | Male Plug |  |  | 1/2" |  |  | 1/2" |  | 2 |  |  |  |  | Brass
22 |  |  | Tee Piece |  |  | 3 x Cu Tube Connection |  |  | 3/8" |  | 7 |  |  |  |  | Brass
23 |  |  | Elbow |  |  | 2 x Cu Tube Connection |  |  | 3/8" |  | 6 |  |  |  |  | Brass
24 |  |  | Male Connector |  |  | Cu Threaded End x Cu Tube Connection |  |  | 1/2" NPT x 3/8" Tube |  | 6 |  |  |  |  | Brass | To Connect Nickel Plated Brass Ball Valves
25 |  |  | PID 2 - Parr Stirred Digester
26 |  |  | Female Connector |  |  | Threaded End x Cu Tube Connection |  |  | 1/4" NPT x 3/8" Tube |  | 1 (Note 1) |  |  |  |  | Brass | To Connect to SS Flexible Hose exsiting 1/4" male thread on hose on site
27 |  |  | PID 4 - RDH Digester
28 |  |  | Straight Coupler |  |  | Medical copper Tube x SS316 Tube |  |  | 3/8" Tube x 3/8" Tube |  | 1 (Note 1) |  |  |  |  | VTC
29 |  |  | Male Connector |  |  | SS Threaded End x SS316 Tube |  |  | 3/8" BSPP x 3/8" Tube |  | 1 (Note 1) |  |  |  |  | VTC | RDH G3/8" Socket

## Compressed Air Line
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-001
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Compressed Air Line Connections Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  |  | Prepared |  |  | Checked |  | Approved |  | Status
A |  |  |  |  | MJ | [6 empty] | Issued for Internal Review
Data Sheet for Compressed Air Line Connections and Tubing
No | Rev | Section | Data | [5 empty] | Description
1 |  | DESIGN DATA | TRANSPORTED FLUID | [7 empty] | Compressed Air
2 |  |  | LOCATION | [7 empty] | Above Ground
3 |  |  | DESIGN LIFE | [7 empty] | 25 years
4 |  |  | PIPELINE DESIGN PRESSURE |  |  |  | Barg |  |  |  | 25
5 |  |  | PIPELINE TEMPERATURE - DESIGN |  |  |  |  | °C | MAXIMUM |  | 65 |  | Note 2 | MINIMUM: | 0
6 |  |  | SERVICE TYPE (Sour/ Non-sour) |  |  |  |  | barg |  |  | Non-sour
7 |  |  | TUBING MATERIAL | [7 empty] | Medical Grade Copper SANS 1453:2011 (Imperial)
8 |  |  | TUBING FITTING MATERIAL | [7 empty] | VTC
9 |  |  | TUBING FITTING THREAD | [7 empty] | NPT and BSP
10 |  |  | TUBING FITTING TYPE | [7 empty] | Compression fitting (Ferrule type) (VTC)
11 |  |  | Notes
12 |  |  | 1 | VTC - VENDOR TO CONFIRM
13 |  |  | 2 | Supplier to confirm tubing for specified Pressures and Temperatures
14
15
16 | [10 empty] | VENDOR TO CONFIRM
17 |  | Material and Quantities | Description |  |  | End Connection |  |  | Size |  | Quantity |  |  |  |  | Connection Material | Notes
18 |  |  | Medical Cu Tube |  |  | 1/2" Medical Grade Copper Tubing |  |  | 1/2" |  | 7 Of 5.5m lenths (Note 2)
19 |  |  | PID 10 - Main Utilities
20 |  |  | Male Connector |  |  | 12/" tube x 1/2" NPT |  |  | 1/2" |  | 2 |  |  |  |  | Brass
21 |  |  | Plug |  |  | 1/2" NPT Plug |  |  | 1/2" |  | 2 |  |  |  |  | Brass
22 |  |  | Tee Piece |  |  | 3 x Cu Tube Connection |  |  | 1/2" |  | 7 |  |  |  |  | Brass
23 |  |  | Elbow |  |  | 2 x Cu Tube Connection |  |  | 1/2" |  | 10 |  |  |  |  | Brass
|  |  | Male Connector |  |  | Cu Threaded End x Cu Tube Connection |  |  | 1/2" NPT x 1/2" Tube |  | 10 |  |  |  |  | Brass | To Connect Nickel Plated Brass Ball Valves
PID 9 - LC Refiner and Valley Beater
25 |  |  | Female Connector |  |  | Cu Threaded End x Cu Tube Connection |  |  | 3/8" NPT x 1/2" Tube |  | 2 |  |  |  |  | Brass | To Connect to Quickfit Air Nipple 3/8"
26 |  |  | Reducing Union |  |  | Threaded End x Flex Hose Nipple |  |  | 1/2" Tube x 3/8" Tube |  | 2 | [5 empty] | To Connect to polyeurethane 3/8" Flex Hose - 1 ftting connect from 1/2" copper to 3/8" polyu tubing
27 |  |  | PID 3 - Flow Through Digester
28 |  |  | Female Connector |  |  | Cu Threaded End x Cu Tube Connection |  |  | 1/4" NPT x 1/2" Tube |  | 1 |  |  |  |  | Brass | To Connect to Quickfit Air Nipple 6mm
PID 2 - Parr Stirred Digester
29 |  |  | Male Quickfit Nipple |  |  | Threaded End x Flex Hose Nipple |  |  | 1/2" Tube x 3/8" Tube |  | 1 | [5 empty] | To Connect to polyeurethane 3/8" Flex Hose -1 ftting connect from 1/2" copper to 3/8" polyu tubing
30 |  |  | PID 4 - RDH Digester
31 |  |  | Straight Coupler |  |  | Medical copper Tube x SS316 Tube |  |  | 1/2" Tube x 3/8" Tube |  | 1 (Note 1) |  |  |  |  | VTC
32 |  |  | Male Connector |  |  | SS Threaded End x SS316 Tube |  |  | 3/8" BSPP x 3/8" Tube |  | 1 (Note 1) |  |  |  |  | VTC | RDH G3/8" Socket

## Municipal Water Line
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-001
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban | [12 empty] | Page 1 of 2
Item: |  |  | Municipal Water Line Connections Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  |  | Prepared |  |  | Checked |  | Approved |  | Status
A |  |  |  |  | MJ | [6 empty] | Issued for Internal Review
Data Sheet for Municipal Water Line Line Connections and Tubing
No | Rev | Section | Data | [5 empty] | Description
|  | DESIGN DATA | TRANSPORTED FLUID | [7 empty] | Potable Water - Municipal Water
1 |  |  | LOCATION | [7 empty] | Above Ground
2 |  |  | DESIGN LIFE | [7 empty] | 25 years
3 |  |  | PIPELINE DESIGN PRESSURE |  |  |  | Barg |  |  |  | 15
4 |  |  | PIPELINE TEMPERATURE - DESIGN |  |  |  |  | °C | MAXIMUM |  | 40 |  | Note 2 | MINIMUM: | 0
5 |  |  | SERVICE TYPE (Sour/ Non-sour) |  |  |  |  | barg |  |  | Non-sour
6 |  |  | TUBING MATERIAL | [7 empty] | SANS 460/2 (Metric and Imperial)
7 | [10 empty] | ASME 31.3 Stainless Steel 316L Piping
8 |  |  | TUBING FITTING MATERIAL | [7 empty] | VTC
9 |  |  | TUBING FITTING THREAD | [7 empty] | NPT and BSP
10 |  |  | TUBING FITTING TYPE | [7 empty] | Compression fitting (Ferrule type) (VTC)
11 |  |  | Notes
12 |  |  | 1 | VTC - VENDOR TO CONFIRM
13 |  |  | 2 | Supplier to confirm tubing for specified Pressures and Temperatures
14
15 | [10 empty] | VENDOR TO CONFIRM
16 |  |  | Description |  |  | End Connection |  |  | Size |  | Quantity |  |  |  |  | Connection Material | Notes
17 |  |  | SANS 460/2 | [5 empty] | 15mm |  | 12 Of 5.5m lenths (Note 2)
18 |  |  | ASME 36.19 SS304 SCH 40 | [5 empty] | 1/2"
19 |  |  | ASME 36.19 SS316 SCH 40 | [5 empty] | 1" |  | 1 of (Note 2)
20 |  |  | ASME 36.19 SS316 SCH 40 | [5 empty] | 20mm |  | 1 of (Note 2)
21 |  |  | PID 11 - Main Utilities
22 |  |  | End Caps |  |  | Cu Tube Connection |  |  | 15mm |  | 5 |  |  |  |  | Brass
23 |  |  | Tee Piece |  |  | 3 x Cu Tube Connection |  |  | 15mm |  | 10 |  |  |  |  | Brass
24 |  |  | Elbow |  |  | 2 x Cu Tube Connection |  |  | 15mm |  | 15 |  |  |  |  | Brass
25 |  |  | Male Connector |  |  | Cu Threaded End x Cu Tube Connection |  |  | 3/4 BSPP male x 15mm Tube |  | 26 |  |  |  |  | Brass | 15MM x 3/4" Male connector To Connect 3/4" Ball Valves and a To Connect 15mm X 3/4" Female to Flow Meter
27 |  |  | PID 2 - Parr Stirred Digester
28 |  |  | Female Connector |  |  | Cu Tube Connection x Cu Threaded End |  |  | 15mm Tube x 1/2" BSPF Thread |  | 1 |  |  |  |  | Brass | To connnect 6mm Flex Hose nipple connection
29 |  |  | Male connector |  |  | 6mm x 1/2" BSP Male Pushin Fittings |  |  | 6mm x 1/2" BSP Male Pushin Fittings |  | 1 |  |  |  |  | VTC | 15mm copper tube to connect to 6mm polyu tube
30 |  |  | Female Connector |  |  | Cu Tube Connection x Cu Threaded End |  |  | 15mm Tube x 1/2" BSPF Thread |  | 1 |  |  |  |  | VTC | 15mm copper tube to connect to 6mm polyu tube
31 |  |  | Male connector |  |  | 6mm x 1/2" BSP Male Pushin Fittings |  |  | 6mm x 1/2" BSP Male Pushin Fittings |  | 1 |  |  |  |  | VTC | To Connect to polyeurethane 6mm Flex Hose
32 |  |  | PID 3 - Flow Through Digester
33 |  |  | Male Connector |  |  | Cu Tube Connection x Cu Threaded End |  |  | 15mm Tube x 25mm BSP Thread |  | 1 |  |  |  |  | Brass | Use thread tape for isolation
34 |  |  | EN1092 SS PN40 Blind (#05) Flange |  |  | DN25 SS316L Flange |  |  | DN25 |  | 1 |  |  |  |  | SS | Flanged Drilled and tap 1" BSPF Thread To suit 15mm copper tube- Thread Tape used as isolation joint between SS Flange and 15mm SANS460/2 tube.
35 |  |  | Male Connector |  |  | 15MM x 3/4 Male connector |  |  | To Connect for female threaded flange |  | 1
36 |  |  | EN1092 SS PN40 Weldneck (#11) Flange |  |  | DN25 (1inch) SS 316L Flange |  |  | DN25 |  | 1 | [5 empty] | To weld onto SS316L Pipe - Bolted to SS Flange on SANS 460/2 tube
37 |  |  | Male Connector |  |  | SS 316L Pipe x SS 316L Threaded End |  |  | 1" SS Tube x 1" NPT Thread |  | 1 |  |  |  |  | VTC | To attach to 1" Female NPT
38 |  |  | PID 6 - Biochar Cooling Tower Make-Up Water
39 |  |  | Male Connector |  |  | Cu Tube Connection x Cu Threaded End |  |  | 15mm Tube x 15mm BSP Thread |  | 1 |  |  |  |  | Brass | To connect 1/2" Flange
40 |  |  | EN1092 SS PN25 Blind (#05) Flange (IMPERIAL) |  |  | 1" SS304 Flange |  |  | 1/2" |  | 1 |  |  |  |  | 304 SS | Drill and tap 3/4" BSP Thread - Thread Tape used as isolation joint between SS Flange and 15mm SANS460/2 tube.
41 |  |  | EN1092 SS PN25 Weldneck (#11) Flange IMPERIAL |  |  | 1" SS304 Flange |  |  | 1/2" |  | 1 |  |  |  |  | SS306 | To be welded to ASME 31.3 SS306 Sch40
42 |  |  | Female Connector |  |  | SS306 SCH40 Pipe Connection x Threaded End |  |  | 1/2" Pipe Connection x 1/2" BSP Thread |  | 1 |  |  |  |  | SS306
43 |  |  | PID 4 - RDH Digester
44 |  |  | Tee Piece |  |  | SS316L Pipe connection x SS316L Pipe connection |  |  | 20mm SS Pipe x 20mm SS Pipe |  | 1 |  |  |  |  | VTC | To attach to 1" Female NPT
45 |  |  | Elbow |  |  | SS316L Pipe connection x SS316L Pipe connection |  |  | 20mm SS Pipe x 20mm SS Pipe |  | 6 |  |  |  |  | VTC
46 |  |  | Male Connector |  |  | Cu Tube Connection x Cu Threaded End |  |  | 15mm Tube x 20mm BSP Thread |  | 1 |  |  |  |  | Brass | Use thread tape for isolation
47 |  |  | EN1092 SS PN40 Blind (#05) Flange METRIC |  |  | DN20 SS316L Flange |  |  | DN20 |  | 1 |  |  |  |  | SS316 | Drill and tap 3/4" BSP Female Thread - Thread Tape ised as isolation joint between SS Flange and Copper pipe.
48 |  |  | EN1092 SS PN40 Weldneck (#11) Flange METRIC |  |  | DN20 SS 316L Flange |  |  | DN20 |  | 3 |  |  |  |  | SS316 | To weld onto SS316L Pipe - Check Bolt positions on RDH Digester Flange before welding.
49 |  |  | PID 12 - Steam Boiler
50 |  |  | Reducing Female Coupler |  |  | Brass Threaded End x Cu Tube Connection |  |  | 3/4" BSP Thread x 15mm Cu Tube |  | 1 |  |  |  |  | Brass | To attach 3/4" Male Brass BSP Ball Valve attached to inlet of feed water tank on steam boiler.

## Hot Water Line
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-001
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Municipal Water Line Connections Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  |  | Prepared |  |  | Checked |  | Approved |  | Status
A |  |  |  |  | MJ | [6 empty] | Issued for Internal Review
Data Sheet for Municipal Water Line Line Connections and Tubing
No | Rev | Section | Data | [5 empty] | Description
1 |  | DESIGN DATA | TRANSPORTED FLUID | [7 empty] | Potable Water - Municipal Water
2 |  |  | LOCATION | [7 empty] | Above Ground
3 |  |  | DESIGN LIFE | [7 empty] | 25 years
4 |  |  | PIPELINE DESIGN PRESSURE |  |  |  | Barg |  |  |  | 15
5 |  |  | PIPELINE TEMPERATURE - DESIGN |  |  |  |  | °C | MAXIMUM |  | 40 |  | Note 2 | MINIMUM: | 0
6 |  |  | SERVICE TYPE (Sour/ Non-sour) |  |  |  |  | barg |  |  | Non-sour
7 |  |  | TUBING MATERIAL | [7 empty] | SANS 460/2 (Metric)
ASME 31.3 Stainless Steel 306L Piping (Imperial)
8 | [10 empty] | ASME 31.3 Stainless Steel 316L Piping (Imperial)
9 |  |  | TUBING FITTING MATERIAL | [7 empty] | VTC
10 |  |  | TUBING FITTING THREAD | [7 empty] | NPT and BSP
11 |  |  | TUBING FITTING TYPE | [7 empty] | Compression fitting (Ferrule type) (VTC)
12 |  |  | Notes
13 |  |  | 1 | VTC - VENDOR TO CONFIRM
14 |  |  | 2 | Supplier to confirm tubing for specified Pressures and Temperatures
15 |  |  | 3 | TBC - To be confirmed
16
17 | [10 empty] | VENDOR TO CONFIRM
18 |  |  | Description |  |  | End Connection |  |  | Size |  | Quantity |  |  |  |  | Connection Material | Notes
19 |  |  | SANS 460/2 |  |  | 22mm Copper Tubing |  |  | 22mm |  | 1 Of 5.5m lenths (Note 2)
|  |  | SANS 460/2 |  |  | 15mm Copper Tubing |  |  | 15mm |  | 10 Of 5.5m lenths (Note 2)
22 |  |  | PID 11 - Main Utilities
23 |  |  | End Caps |  |  | Cu Tube Connection |  |  | 15mm |  | 2 |  |  |  |  | Brass
|  |  | End Caps |  |  | Cu Tube Connection |  |  | 22mm |  | 2 |  |  |  |  | Brass
|  |  | Reducing Straight Coupler |  |  | 2 x Cu Tube Connection |  |  | 15mm x 22mm |  | 3 |  |  |  |  | Brass
24 |  |  | Tee Piece |  |  | 3 x Cu Tube Connection |  |  | 22mm |  | 1 |  |  |  |  | Brass
|  |  | Elbow |  |  | 2 x Cu Tube Connection |  |  | 22mm |  | 5 |  |  |  |  | Brass
25 |  |  | Elbow |  |  | 2 x Cu Tube Connection |  |  | 15mm |  | 10 |  |  |  |  | Brass
|  |  | Male Connector |  |  | Cu Threaded End x Cu Tube Connection |  |  | 3/4" BSPP x 22mm Tube |  | 2 |  |  |  |  | Brass | To Connect Nickel Plated Brass Ball Valves and a Flow Meter
26 |  |  | Male Connector |  |  | Cu Threaded End x Cu Tube Connection |  |  | 3/4" BSPP x 15mm Tube |  | 8 |  |  |  |  | Brass | To Connect Nickel Plated Brass Ball Valves and a Flow Meter
27 |  |  | PID 8 - Waste Paper Recycler
28 |  |  | Female Connector |  |  | Cu Tube Connection x Cu Threaded End |  |  | 15mm Tube x 3/4" BSP Thread |  | 2 |  |  |  |  | Brass | To Connect Nickel Plated Brass Ball Valves and a Flow Meter
30 |  |  | PID 9 - Valley Beater
31 |  |  | Male Connector |  |  | Cu Threaded End x Cu Tube Connection |  |  | 3/4" BSPP x 15mm Tube |  | 2 |  |  |  |  | Brass | To Connect Nickel Plated Brass Ball Valves and a Flow Meter
32 |  |  | Female Connector |  |  | Cu Tube Connection x Cu Threaded End |  |  | 15mm Tube x 3/4"BSP Thread |  | 2 |  |  |  |  | Brass | To Connect Nickel Plated Brass Ball Valves and a Flow Meter

## Steam Line
Project |  |  | BIDF Expansion
Document No: |  |  | 21050-CSI-ME-DAS-001
Location: |  |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Item: |  |  | Municipal Water Line Connections Data Sheet
Page: |  |  | 1 of 1
Revision Tracking
Rev No. |  | Date |  |  | Prepared |  |  | Checked |  | Approved |  | Status
A |  |  |  |  | MJ | [6 empty] | Issued for Internal Review
Data Sheet for Municipal Water Line Line Connections and Tubing and Piping
No | Rev | Section | Data | [5 empty] | Description
1 |  | DESIGN DATA | TRANSPORTED FLUID | [7 empty] | STEAM
2 |  |  | LOCATION | [7 empty] | Above Ground
3 |  |  | DESIGN LIFE | [7 empty] | 25 years
4 |  |  | PIPELINE DESIGN PRESSURE |  |  |  | Barg |  |  |  | 25
5 |  |  | PIPELINE TEMPERATURE - DESIGN |  |  |  |  | °C | MAXIMUM |  | 220 |  | Note 2 | MINIMUM: | 0
6 |  |  | SERVICE TYPE (Sour/ Non-sour) |  |  |  |  | barg |  |  | Non-sour
7 |  |  | PIPING MATERIAL | [7 empty] | ASTM A 106 Gr B
8 |  |  | FITTING MATERIAL | [7 empty] | VTC
9 |  |  | FITTING TYPE | [7 empty] | Socket Weld
10 |  |  | Notes
11 |  |  | 1 | VTC - VENDOR TO CONFIRM
12 |  |  | 2 | Supplier to confirm tubing for specified Pressures and Temperatures
13 |  |  | 3 | TBC - To be confirmed
14 |  |  | 4 | SW - Socket Weld
15 | [10 empty] | VENDOR TO CONFIRM
16 |  |  | Description |  |  | End Connection |  |  | Size |  | Quantity |  |  |  |  | Connection Material | Notes
17 |  |  | ASME 31.3 CS A106 Gr B SCH 40 | [5 empty] | 1 1/2" SCH40 |  | 6 Of 6m lenths (Note 2) |  |  |  |  | ASME A106 Gr B | Main Line Piping
18 |  |  | ASME 31.3 CS A106 Gr B SCH40 | [5 empty] | 1/2" SCH40 |  | 2 Of 6m lenths (Note 2) |  |  |  |  | ASME A106 Gr B | Steam Trap Piping
19 |  |  | ASME 31.3 CS A106 Gr B SCH40 | [5 empty] | 3/8" SCH40 |  | 2 Of 6m lenths (Note 2) |  |  |  |  | ASME A106 Gr B | RDH Digester Piping Line
20 |  |  | PID 12 - Steam Boiler
21 |  |  | EN1092 PN25 RF Blind Flange (#5) IMPERIAL |  |  | 2" RF BLIND FLANGE |  |  | 2" |  | 1 |  |  |  |  | Carbon Steel | Drill 1 1/2" SCH 40 Hole Thru TO weld to SCH40 Pipe - To bolt to 2" Boiler EN1092 2500/3 Steam Flange
22 |  |  | End Caps |  |  | A106 Gr B CS SCH40 Pipe Connection SW |  |  | 1 1/2" |  | 4 |  |  |  |  | ASTM A234
23 |  |  | End Caps |  |  | A106 Gr B CS SCH40 Pipe Connection SW |  |  | 3/8" |  | 1 |  |  |  |  | ASTM A234
24 |  |  | Reducing Tee-Piece |  |  | A106 Gr B CS SCH40 SW x A106 Gr B CS SCH40 SW |  |  | 2x1.5" Pipe by 1x3/8" Pipe |  | 1 |  |  |  |  | ASTM A234
25 |  |  | Reducing Tee-Piece |  |  | A106 Gr B CS SCH40 SWx A106 Gr B CS SCH40 SW |  |  | 2x1.5" Pipe by 1x1/2" Pipe |  | 2 |  |  |  |  | ASTM A234
26 |  |  | 90 degree Angles |  |  | A106 Gr B CS SCH40 SW x A106 Gr B CS SCH40 SW |  |  | 1.5" Pipe x 1.5" Pipe |  | 4 |  |  |  |  | ASTM A234
27 |  |  | 90 degree Angles |  |  | A106 Gr B CS SCH40 SW x A106 Gr B CS SCH40 SW |  |  | 0.5" Pipe x 0.5" Pipe |  | 12 |  |  |  |  | ASTM A234
28 |  |  | EN1092 PN25 RF Slip On Flange (#1) IMPERIAL |  |  | 1.5" RF SLIP ON FLANGE |  |  | 1.5" |  | 2 |  |  |  |  | ASTM A234 | For steam trap low point drain ball valve
29 |  |  | EN1092 NP25 RF Blind Flange (#5) IMPERIAL |  |  | 1.5" RF BLIND FLANGE |  |  | 1.5" |  | 2 |  |  |  |  | ASTM A234 | Drill 1/2" SCH 40 Hole Thru TO weld to SCH40 Pipe - To bolt to 1.5" EN 1092-1 STEAM TRAP DRAIN BALL VALVE PIPE
30 |  |  | Tee-Piece |  |  | A106 Gr B CS SCH40 SWx A106 Gr B CS SCH40 SW |  |  | 1.5" |  | 5 |  |  |  |  | ASTM A234 | STEAM TRAP AND AIR VENT BRANCH, PLUS MAINLINE BRANCHES
31 |  |  | Tee-Piece |  |  | A106 Gr B CS SCH40 SWx A106 Gr B CS SCH40 SW |  |  | 0.5" |  | 6 |  |  |  |  | ASTM A234
32 | [15 empty] | ASTM A234
33 |  |  | PID 4 - RDH DIGESTER
34 |  |  | EN1092 PN40 RF Slip On Flange (#1) METRIC |  |  | DN20 RF SLIP ON FLANGE |  |  | DN 20 |  | 1 |  |  |  |  | ASTM A234 | To connect steam line to RDH digester