## 0.5" Steam Boiler Steam Trap
Project |  | BIDF Expansion |  |  |  |  | Page 1 of 1
Document No. |  | 21050-CSI-ME-DAS-003
Location |  | UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban
Steam Traos - Steam boiler
Revision Status
Rev No. |  | Date | Prepared By | Revised Sheet | Revision | Approvals
[6 empty] | Checked By | Approved By
A |  | 2020-02-11 | MJ | All | Issued for Internal Review
1 | Description |  |  | Thermodynamic Steam Trap
2 | Reference P&ID |  |  | 19088-PS2-PR-PID-012
3 | Item Number:
4 | Quantity: |  |  | 2
5 | Service: |  |  | Particle Removal for Steam Line
6 | Fluid: |  |  | Steam |  | Water
7 | Standard type: |  |  | European Pressure Equipment Directive 97/23/EC
8 | Flowrate: |  | min: | 0 |  |  |  | kg/hr
|  |  | Operating | 108 |  |  |  | kg/hr
|  |  | max: | 200 |  |  |  | kg/hr
|  |  | design: | 300 |  |  |  | kg/hr
9 | Temperature: |  | min: | 0 |  |  |  | oC
|  |  | max: | 190 |  |  |  | oC
|  |  | design (min/max): | 220 |  |  |  | oC
10 | Pressure: |  | min: | 100 |  |  |  | kPa
|  |  | max: | 1700 |  |  |  | kPa
|  |  | design: | 1850 |  |  |  | kPa
11 | Class |  |  | 300
12 | Connection Type: |  | inlet: | 0.5" Socket Weld Ends - ASME SCH 40 Pipe
|  |  | outlet: | 0.5" Socket Weld Ends - ASME SCH 40 Pipe
13 | Closure Seal: |  |  | Reinforced exfoliated graphite
14 | Orientation of Strainer Filter: |  |  | Y-Type
15 | Perforations Size: |  |  | 0.8mm |  |  |  | kPa
16 | Corrosion Allowance: |  |  | 1 |  |  |  | mm
17 | Type of Closure: |  |  | Bolted
18 | Material: |  | Body: | Carbon Steel - ASTM A105 / A106
|  |  | Cap: | Carbon Steel - ASTM A105 / A106
|  |  | Cap Gasket: | VTC
|  |  | Strainer Screen: | Stainless Steel - A240 316L
19 | Relief Valve: |  |  | None
20 | Drain Line: |  |  | None
General Requirements
21 | 1 - Weld Quality Requirements in accordance with ISO 3834
22 | 2- Test Report ans Material Certification Required
23 | 3 - Seals and Gaskets to to be compatible with Steam