## Bill of Quantities B15
C.S.I.R. Building Number 15 C.S.I.R. Buidin
Page 1
BILL NO. 1 : Laboratory Gas Installation First Floor
ITEM No. | DESCRIPTION | UNIT | QTY | RATE | TOTAL
This bill shall be priced to provide a complete installation
1 | Supply, Install, Test and Commission the Laboratory Gas Installation
1.1 | Gasbank
| Supply and install multistage regulator type Tescom 44-1100 for a 2x1 manual change over manifold, complete with braided stainless steel serpentine, pressure gauges, midrail and chain for Hydrogen Gas downstream pressure 200 bar | no. | 1 |  | 0
| Relocate and install existing multistage regulator type Tescom 443464S24 for a 2x1 manual change over manifold, complete with braided stainless steel serpentine, pressure gages, midrail and chain for Hydrogen Gas. | no. | 1 |  | 0
| Supply and install multistage regulator type Tescom 44-1100 for a 2x1 manual change over manifold, complete with braided stainless steel serpentine, pressure gauges, midrail and chain for Hydrogen / Carbon Dioxide downstream pressure 200 bar. | no. | 1 |  | 0
| Supply and install multistage regulator type Tescom 44-1100 for a 2x1 manual change over manifold, complete with braided stainless steel serpentine, pressure gauges, midrail and chain for Nitrogen Gas downstream pressure 200 bar. | no. | 1 |  | 0
East Gasbank for Ground Floor
| Remove existing not in use existing Nitrogen 2x1 manual change over manifold and hand over to the client. | no. | 1 |  | 0
| Extend the existing N2 pipework through wall and tie into the West Gasbank for First Floor existing N2 main from the existing Nitrogen 2x1 manual change over manifold for First floor. Cut in with a T - piece and install a globe isolating | no. | 1 |  | 0
1.2 | MeOH Reactor
| Supply and install end of use regulator type Teskom 44-1100 Stainless Steel complete with pressure gauge and isolating valve for Nitrogen Gas suitable for 200 bar working pressure. | no. | 1 |  | 0
| Supply and install end of use regulator type Teskom 44-1100 Stainless Steel complete with pressure gauge and isolating valve for Hydrogen Gas suitable for 200 bar working pressure. | no. | 1 |  | 0
| Supply and install end of use regulator type Teskom 44-1100 Stainless Steel complete with pressure gauge and isolating valve for Hydrogen / Carbon Dioxide Gas suitable for 200 bar working pressure. | no. | 1 |  | 0
1.3 | Continuous Flow Reactor
| Supply and install end of use regulator type Teskom 44-1100 Stainless Steel complete with pressure gauge and isolating valve for Hydrogen Gas suitable for 200 bar working pressure. | no. | 1 |  | 0
| Supply and install end of use regulator type Teskom 44-1100 Stainless Steel complete with pressure gauge and isolating valve for Hydrogen / Carbon Dioxide Gas suitable for 200 bar working pressure. | no. | 1 |  | 0
| Supply and install end of use regulator type Teskom 44-1100 Stainless Steel complete with pressure gauge and isolating valve for Nitrogen Gas suitable for 200 bar working pressure. | no. | 1 |  | 0
| Globe isolating valve Oxygen clean suitable for 200 bar working presure | no. | 5 |  | 0
| Oxygen clean non return valve suitable fro 200 bar working pressure | no. | 3 |  | 0
1.4 | PCT Pro
| Supply and install end of use regulator type Teskom 44-1100 Stainless Steel complete with pressure gauge and isolating valve for Hydrogen Gas suitable for 200 bar | no. | 1 |  | 0
| Globe isolating valve Oxygen clean suitable for 200 bar working presure | no. | 2 |  | 0
| Oxygen clean non return valve suitable fro 200 bar working pressure | no. | 2 |  | 0
1.5 | Gas Bank |  |  |  | 0
| Relocated existing Hydrogen manifold |  |  |  | 0
| Solenoid valve normally closed Oxygen clean intrinsic safe class 1 devision 1 suitable for working pressure of 50 bar | no. | 1 |  | 0
| Flashback Arrestor Oxygen clean suitable for 50 bar working presure | no. | 1 |  | 0
| Globe isolating valve Oxygen clean suitable for 50 bar working presure | no. | 1 |  | 0
1.6 | New High Pressure Hydrogen manifold
| Solenoid valve normally closed Oxygen clean intrinsic safe class 1 devision 1 suitable for working pressure of 200 bar | no. | 1 |  | 0
| Flashback Arrestor Oxygen clean suitable for 200 bar working presure | no. | 1 |  | 0
| Globe isolating valve Oxygen clean suitable for 200 bar working presure | no. | 1 |  | 0
| Emergency Globe isolating valve Oxygen clean suitable for 200 bar working presure | no. | 1 |  | 0
New High Pressure Hydrogen / Carbon Dioxide manifold
| Solenoid valve normally closed Oxygen clean intrinsic safe class 1 devision 1 suitable for working pressure of 200 bar | no. | 1 |  | 0
| Flashback Arrestor Oxygen clean suitable for 200 bar working presure | no. | 1 |  | 0
| Globe isolating valve Oxygen clean suitable for 200 bar | no. | 1 |  | 0
| Emergency Globe isolating valve Oxygen clean suitable for 200 bar working presure | no. | 1 |  | 0
| Emergency Globe isolating valve Oxygen clean suitable for 200 bar working presure | no. | 1 |  | 0
MeOH reactor
New High Pressure Nitrogen
| Globe isolating valve Oxygen clean suitable for 200 bar working presure | no. | 1 |  | 0
New High Pressure Hydrogen / Carbon Dioxide
| Supply and install end of use regulator type Teskom 44-1100 Stainless Steel complete with pressure gauge and isolating valve for Hydrogen / Carbon Dioxide Gas suitable for 200 bar working pressure. | no. | 1 |  | 0
| Flashback Arrestor Oxygen clean suitable for 200 bar working presure | no. | 4 |  | 0
| Globe isolating valve Oxygen clean suitable for 200 bar working presure | no. | 4 |  | 0
| Oxygen clean 4 Way Isolating valve suitable for 200 bar working pressure | no. | 1 |  | 0
| Oxygen clean Non Return valve suitable for 200 bar working pressure | no. | 3 |  | 0
New High Pressure Hydrogen
| Supply and install end of use regulator type Teskom 44-1100 Stainless Steel complete with pressure gauge and isolating valve for Hydrogen Gas suitable for 200 bar working pressure. | no. | 1 |  | 0
| Flashback Arrestor Oxygen clean suitable for 200 bar working presure | no. | 1 |  | 0
| Globe isolating valve Oxygen clean suitable for 200 bar working presure | no. | 4 |  | 0
| 3 way regulating valve Oxygen clean suitable for 200 bar working presure | no. | 2 |  | 0
1.7 | Flow Control Regulators
| Supply and install regulator type Teskom 44-2200 Stainless Steel complete with pressure gauge and isolating valves before and after the regulators for Nitrogen; Hydrogen; Hydrogen / Carbon Dioxide Gas suitable for 200 bar working pressure. | no. | 3 |  | 0
1.8 | Pipework and Fittings
Reloction of existing Hydrogen Manifold
Remove existing redundant piping and hand over to the client
| 3/8" 316 Stainless Steel Piping | m | 4 |  | 0
| 3/8" 316 Stainless Steel Couplers | no. | 0 |  | 0
| 3/8" 316 Stainless Steel Elbows | no. | 6 |  | 0
| 3/8" 316 Stainless Steel Tees | no. | 0 |  | 0
| 7/8" P.V.C. Sleeves | no. | 1 |  | 0
| 3/8" Pipe Holder Bats | no. | 6 |  | 0
New High Pressure Hydrogen
| 1/4" 316 Stainless Steel Piping | m | 52 |  | 0
| 1/4" 316 Stainless Steel Elbows | no. | 24 |  | 0
| 1/4" 316 Stainless Steel Tees | no. | 3 |  | 0
| 1/4" Pipe Holder Bats | no. | 50 |  | 0
| 7/8" P.V.C. Sleeves | no. | 6 |  | 0
New High Pressure Hydrogen / Carbon Dioxide
| 1/4" 316 Stainless Steel Piping | m | 52 |  | 0
| 1/4" 316 Stainless Steel Elbows | no. | 24 |  | 0
| 1/4" 316 Stainless Steel Tees | no. | 3 |  | 0
| 1/4" Pipe Holder Bats | no. | 50 |  | 0
| 7/8" P.V.C. Sleeves | no. | 6 |  | 0
New High Pressure Nitrogen
| 1/4" 316 Stainless Steel Piping | m | 42 |  | 0
| 1/4" 316 Stainless Steel Elbows | no. | 20 |  | 0
| 1/4" 316 Stainless Steel Tees | no. | 3 |  | 0
| 1/4" Pipe Holder Bats | no. | 45 |  | 0
| 7/8" P.V.C. Sleeves | no. | 6 |  | 0
Fittings
| 1/4" 316 Stainless Steel Fittings | no. | 24 |  | 0
1.9 | CABLE TRAY
| 200 x 100 cable tray to be mounted against columns and wall to house new gas mains | m | 14 |  | 0
1.1 | UPS
| Supply and install UPS System to facitate power to solenoid valves, alarm panel. | no. | 1 |  | 0
1.11 | Upgrade existing alarm panel and system
| Upgrade existing alarm panel and system to link to solenoid valves, low pressure sensors, new and exisitng panic buttons, new and existing Hydrogen gas detectors. | no. | 1 |  | 0
1.12 | In line Pressure switches
| supply and install low pressure switches linked to the alarm panel system to indicate warning in case of a rapid pressure drop in the gas main. | item | 1 |  | 0
1.13 | Additional Panic Button
| Supply and install additonal panic button as indicated on the drawing and link to existing panic button and alarm system | item | 1 |  | 0
1.14 | Additional gas detection sensors
| Supply and install hydrogen gas detectors in the Hydrogen laboratory to detect any gas leaks at the various testing equipment and link to existing gas detection system and alarm panel | no | 3 |  | 0
1.15 | Additional 4,5 kg DCP fire extinguishers
| Supply and install 4,5 kg DCP fire extinguishers at the laboratory as indicated on the drawing | no. | 1 |  | 0
1.16 | Additional 9 kg DCP fire extinguishers
| Supply and install 9 kg DCP fire extinguishers at the gasbank as indicated on the drawing | no. | 1 |  | 0
1.17 | Safety Signage
| Supply and install new safety signage at gthe gasbank and at the laboratory as per drawing | item | 1 |  | 0
1.18 | Pressure testing of laboratory gas installation | item | 1 |  | 0
1.19 | Testing and Commissioning of laboratory gas installation | item | 1 |  | 0
1.2 | Operating and maintenance manuals | item | 1 |  | 0
1.21 | Staff training | item | 1 |  | 0
1.22 | Builders work
All builders work forms part of this contract
| Excavate in soft soil foundations of 600mm x 250mm deep. Excavated soil, grass and plants to be removed off site, to a legal dumping site. | m3 | 3 |  | 0
| Pour 30 MPa concrete foundation in trench | m3 | 3 |  | 0
| Floor slab to match existing concrete floor slab. | m3 | 2 |  | 0
| Brickwork to match existing brickwork. (screen walls) | m2 | 8 |  | 0
| Roof slab to match existing concrete work | m2 | 0 |  | 0
| Steelwork to match existing steelwork | m2 | 0 |  | 0
All paint products used are to be Plascon Products or approved equal
| Prepare and spray paint with Plascon Galvogrip and two coats of Plascon Velvaglo or apprved equal on steelwork | m2 | 16.4 |  | 0
| Prepare and spray paint with Plascon Galvogrip and two coats of Plascon Velvaglo or approved equal on brickwork | m2 | 36 |  | 0
1.23 | Make good penetrations through outer wall and paint wall | no | 9 |  | 0
| Remove all redundant rubble from site and move to legal dumping site. | Item | 1 |  | 0
| P&G | Item | 1 |  | 0
| SUB TOTAL |  |  |  | 0
| Contigency | 10% |  |  | 0
| SUB TOTAL |  |  |  | 0
| V.A.T. | 15% |  |  | 0
| TOTAL |  |  |  | 0